## RS0001
RS0001: Liquid-Cooled Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 2.0.0 |  | ✓
| description | ASHRAE 90.1-2019 Addendum 'bd' curve set 'V': 0.0-150.0 ton, 4.45 COP, 5.20 IPLV liquid-cooled, positive displacement compressor chiller |  | ✓
| id | b0b4a5a5-73c0-4740-9032-63fd6682d541 |  | ✓
| data_timestamp | 2024-02-22T13:52Z |  | ✓
| data_version | 2 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2019 Addendum 'bd' curve set 'V' for Performance Rating Method (PRM)
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | SCROLL
performance |  |  |  | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
performance.condenser_liquid_type |  |  |  | ✓
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
| condenser_fouling_factor | 0 | m2-K/W | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| cycling_degradation_coefficient | 0 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
performance.performance_map_evaporator_liquid_pressure_differential |  | $performance_map_evaporator_liqu |  | ✓
performance.performance_map_condenser_liquid_pressure_differential |  | $performance_map_condenser_liqui |  | ✓
performance.scaling
| maximum | 2 | -
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on A20: Type of liquid in evaporator
Note on A21: An array of all liquid components within the liquid mixture
Note on B22: Defines whether concentration is defined on a volume or mass basis
Note on A23: Type of liquid in condenser
Note on A24: An array of all liquid components within the liquid mixture
Note on B25: Defines whether concentration is defined on a volume or mass basis
Note on B26: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B27: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B28: Type of compressor speed control
Note on B29: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A30: Data group describing cooling performance over a range of conditions
Note on A31: Data group describing standby performance
Note on A32: Data group describing the liquid pressure differential through the evaporator
Note on A33: Data group describing the liquid pressure differential through the condenser
Note on A34: Specifies the range the performance data can be scaled to represent different capacity equipment
Note on B35: Maximum scaling factor

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | oil_cooler_heat | auxiliary_heat | operation_state
m3/s | K | m3/s | K | - | W | W | W | W | W | -
0.011302 | 277.0389 | 0.015021 | 285.9278 | 1 | 16641.9527 | 67088.7666 | 83730.7193 | 0 | 0 | NORMAL
0.011302 | 277.0389 | 0.015021 | 285.9278 | 2 | 23452.4354 | 134177.5332 | 157629.9686 | 0 | 0 | NORMAL
0.011302 | 277.0389 | 0.015021 | 285.9278 | 3 | 32894.9993 | 201266.2998 | 234161.2992 | 0 | 0 | NORMAL
0.011302 | 277.0389 | 0.015021 | 285.9278 | 4 | 44969.6446 | 268355.0664 | 313324.711 | 0 | 0 | NORMAL
0.011302 | 277.0389 | 0.015021 | 295.0019 | 1 | 18763.1186 | 63679.592 | 82442.7107 | 0 | 0 | NORMAL
0.011302 | 277.0389 | 0.015021 | 295.0019 | 2 | 26441.6583 | 127359.1841 | 153800.8424 | 0 | 0 | NORMAL
0.011302 | 277.0389 | 0.015021 | 295.0019 | 3 | 37087.7616 | 191038.7761 | 228126.5377 | 0 | 0 | NORMAL
0.011302 | 277.0389 | 0.015021 | 295.0019 | 4 | 50701.4285 | 254718.3681 | 305419.7967 | 0 | 0 | NORMAL
0.011302 | 277.0389 | 0.015021 | 304.0759 | 1 | 21668.0939 | 58228.9239 | 79897.0178 | 0 | 0 | NORMAL
0.011302 | 277.0389 | 0.015021 | 304.0759 | 2 | 30535.4535 | 116457.8478 | 146993.3013 | 0 | 0 | NORMAL
0.011302 | 277.0389 | 0.015021 | 304.0759 | 3 | 42829.8258 | 174686.7717 | 217516.5975 | 0 | 0 | NORMAL
0.011302 | 277.0389 | 0.015021 | 304.0759 | 4 | 58551.2108 | 232915.6956 | 291466.9064 | 0 | 0 | NORMAL
0.011302 | 277.0389 | 0.015021 | 313.15 | 1 | 24377.4622 | 50736.7622 | 75114.2244 | 0 | 0 | NORMAL
0.011302 | 277.0389 | 0.015021 | 313.15 | 2 | 34353.5922 | 101473.5244 | 135827.1166 | 0 | 0 | NORMAL
0.011302 | 277.0389 | 0.015021 | 313.15 | 3 | 48185.2471 | 152210.2866 | 200395.5337 | 0 | 0 | NORMAL
0.011302 | 277.0389 | 0.015021 | 313.15 | 4 | 65872.4268 | 202947.0488 | 268819.4756 | 0 | 0 | NORMAL
0.011302 | 280.9278 | 0.015021 | 285.9278 | 1 | 16819.0793 | 75694.8568 | 92513.9361 | 0 | 0 | NORMAL
0.011302 | 280.9278 | 0.015021 | 285.9278 | 2 | 23702.0485 | 151389.7135 | 175091.762 | 0 | 0 | NORMAL
0.011302 | 280.9278 | 0.015021 | 285.9278 | 3 | 33245.1132 | 227084.5703 | 260329.6835 | 0 | 0 | NORMAL
0.011302 | 280.9278 | 0.015021 | 285.9278 | 4 | 45448.2735 | 302779.4271 | 348227.7005 | 0 | 0 | NORMAL
0.011302 | 280.9278 | 0.015021 | 295.0019 | 1 | 19112.9291 | 72332.2208 | 91445.1499 | 0 | 0 | NORMAL
0.011302 | 280.9278 | 0.015021 | 295.0019 | 2 | 26934.6238 | 144664.4416 | 171599.0654 | 0 | 0 | NORMAL
0.011302 | 280.9278 | 0.015021 | 295.0019 | 3 | 37779.2078 | 216996.6624 | 254775.8702 | 0 | 0 | NORMAL
0.011302 | 280.9278 | 0.015021 | 295.0019 | 4 | 51646.6813 | 289328.8832 | 340975.5645 | 0 | 0 | NORMAL
0.011302 | 280.9278 | 0.015021 | 304.0759 | 1 | 22565.509 | 66928.0913 | 89493.6002 | 0 | 0 | NORMAL
0.011302 | 280.9278 | 0.015021 | 304.0759 | 2 | 31800.1229 | 133856.1825 | 165656.3054 | 0 | 0 | NORMAL
0.011302 | 280.9278 | 0.015021 | 304.0759 | 3 | 44603.6842 | 200784.2738 | 245387.958 | 0 | 0 | NORMAL
0.011302 | 280.9278 | 0.015021 | 304.0759 | 4 | 60976.1928 | 267712.3651 | 328688.5579 | 0 | 0 | NORMAL
0.011302 | 280.9278 | 0.015021 | 313.15 | 1 | 26229.5671 | 59482.4682 | 85712.0352 | 0 | 0 | NORMAL
0.011302 | 280.9278 | 0.015021 | 313.15 | 2 | 36963.6447 | 118964.9364 | 155928.5811 | 0 | 0 | NORMAL
0.011302 | 280.9278 | 0.015021 | 313.15 | 3 | 51846.1749 | 178447.4045 | 230293.5795 | 0 | 0 | NORMAL
0.011302 | 280.9278 | 0.015021 | 313.15 | 4 | 70877.1578 | 237929.8727 | 308807.0305 | 0 | 0 | NORMAL
0.011302 | 284.8167 | 0.015021 | 285.9278 | 1 | 16990.6631 | 79863.1583 | 96853.8214 | 0 | 0 | NORMAL
0.011302 | 284.8167 | 0.015021 | 285.9278 | 2 | 23943.8505 | 159726.3167 | 183670.1672 | 0 | 0 | NORMAL
0.011302 | 284.8167 | 0.015021 | 285.9278 | 3 | 33584.2711 | 239589.475 | 273173.7461 | 0 | 0 | NORMAL
0.011302 | 284.8167 | 0.015021 | 285.9278 | 4 | 45911.9247 | 319452.6333 | 365364.5581 | 0 | 0 | NORMAL
0.011302 | 284.8167 | 0.015021 | 295.0019 | 1 | 19155.2641 | 76547.061 | 95702.325 | 0 | 0 | NORMAL
0.011302 | 284.8167 | 0.015021 | 295.0019 | 2 | 26994.2837 | 153094.1219 | 180088.4057 | 0 | 0 | NORMAL
0.011302 | 284.8167 | 0.015021 | 295.0019 | 3 | 37862.8884 | 229641.1829 | 267504.0714 | 0 | 0 | NORMAL
0.011302 | 284.8167 | 0.015021 | 295.0019 | 4 | 51761.0783 | 306188.2439 | 357949.3222 | 0 | 0 | NORMAL
0.011302 | 284.8167 | 0.015021 | 304.0759 | 1 | 22682.1202 | 71189.4701 | 93871.5903 | 0 | 0 | NORMAL
0.011302 | 284.8167 | 0.015021 | 304.0759 | 2 | 31964.4556 | 142378.9401 | 174343.3957 | 0 | 0 | NORMAL
0.011302 | 284.8167 | 0.015021 | 304.0759 | 3 | 44834.1816 | 213568.4102 | 258402.5918 | 0 | 0 | NORMAL
0.011302 | 284.8167 | 0.015021 | 304.0759 | 4 | 61291.2981 | 284757.8802 | 346049.1783 | 0 | 0 | NORMAL
0.011302 | 284.8167 | 0.015021 | 313.15 | 1 | 26656.1442 | 63790.3856 | 90446.5298 | 0 | 0 | NORMAL
0.011302 | 284.8167 | 0.015021 | 313.15 | 2 | 37564.7925 | 127580.7711 | 165145.5636 | 0 | 0 | NORMAL
0.011302 | 284.8167 | 0.015021 | 313.15 | 3 | 52689.3605 | 191371.1567 | 244060.5172 | 0 | 0 | NORMAL
0.011302 | 284.8167 | 0.015021 | 313.15 | 4 | 72029.8484 | 255161.5423 | 327191.3907 | 0 | 0 | NORMAL
0.011302 | 288.7056 | 0.015021 | 285.9278 | 1 | 17487.7561 | 79593.6713 | 97081.4274 | 0 | 0 | NORMAL
0.011302 | 288.7056 | 0.015021 | 285.9278 | 2 | 24644.3718 | 159187.3426 | 183831.7145 | 0 | 0 | NORMAL
0.011302 | 288.7056 | 0.015021 | 285.9278 | 3 | 34566.8406 | 238781.0139 | 273347.8545 | 0 | 0 | NORMAL
0.011302 | 288.7056 | 0.015021 | 285.9278 | 4 | 47255.1624 | 318374.6852 | 365629.8476 | 0 | 0 | NORMAL
0.011302 | 288.7056 | 0.015021 | 295.0019 | 1 | 19284.0143 | 76324.1126 | 95608.1268 | 0 | 0 | NORMAL
0.011302 | 288.7056 | 0.015021 | 295.0019 | 2 | 27175.7231 | 152648.2251 | 179823.9482 | 0 | 0 | NORMAL
0.011302 | 288.7056 | 0.015021 | 295.0019 | 3 | 38117.3801 | 228972.3377 | 267089.7178 | 0 | 0 | NORMAL
0.011302 | 288.7056 | 0.015021 | 295.0019 | 4 | 52108.9853 | 305296.4502 | 357405.4355 | 0 | 0 | NORMAL
0.011302 | 288.7056 | 0.015021 | 304.0759 | 1 | 22474.6571 | 71013.0602 | 93487.7174 | 0 | 0 | NORMAL
0.011302 | 288.7056 | 0.015021 | 304.0759 | 2 | 31672.0912 | 142026.1205 | 173698.2117 | 0 | 0 | NORMAL
0.011302 | 288.7056 | 0.015021 | 304.0759 | 3 | 44424.1036 | 213039.1807 | 257463.2844 | 0 | 0 | NORMAL
0.011302 | 288.7056 | 0.015021 | 304.0759 | 4 | 60730.6943 | 284052.241 | 344782.9353 | 0 | 0 | NORMAL
0.011302 | 288.7056 | 0.015021 | 313.15 | 1 | 26176.7618 | 63660.5144 | 89837.2762 | 0 | 0 | NORMAL
0.011302 | 288.7056 | 0.015021 | 313.15 | 2 | 36889.2296 | 127321.0287 | 164210.2584 | 0 | 0 | NORMAL
0.011302 | 288.7056 | 0.015021 | 313.15 | 3 | 51741.7984 | 190981.5431 | 242723.3415 | 0 | 0 | NORMAL
0.011302 | 288.7056 | 0.015021 | 313.15 | 4 | 70734.4682 | 254642.0575 | 325376.5257 | 0 | 0 | NORMAL
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on J3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).
Note on K3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation

## performance_map_evaporator_liqu
performance.performance_map_evaporator_liquid_pressure_differential
grid_variables |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | evaporator_liquid_differential_pressure
m3/s | K | Pa
0.011302 | 277.0389 | 15000
0.011302 | 280.9278 | 15000
0.011302 | 284.8167 | 15000
0.011302 | 288.7056 | 15000
Note on A2: Data group defining the grid variables for the evaporator liquid pressure differential
Note on C2: Data group defining the lookup variables for the evaporator liquid pressure differential
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Pressure difference across the evaporator

## performance_map_condenser_liqui
performance.performance_map_condenser_liquid_pressure_differential
grid_variables |  | lookup_variables
condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | condenser_liquid_differential_pressure
m3/s | K | Pa
0.015021 | 285.9278 | 15000
0.015021 | 295.0019 | 15000
0.015021 | 304.0759 | 15000
0.015021 | 313.15 | 15000
Note on A2: Data group defining the grid variables for the condenser liquid pressure differential
Note on C2: Data group defining the lookup variables for the condenser liquid pressure differential
Note on A3: Condenser liquid flow
Note on B3: Entering condenser liquid temperature
Note on C3: Pressure difference across the condenser