## RS0004
RS0004: Air-to-Air Direct Expansion Refrigerant System
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0004 |  | ✓
| schema_version | 2.0.0 |  | ✓
| description | 36.6 kBtu/h, 3.65 COP, 0.73 SHR cooling coil |  | ✓
| id | 77cad429-e628-43f6-996a-473e36f8c01f |  | ✓
| data_timestamp | 2024-02-22T15:24Z |  | ✓
| data_version | 2 |  | ✓
| data_source | https://github.com/bigladder/resdx
| disclaimer | This data is synthetic and does not represent any physical products.
performance |  |  |  | ✓
| compressor_speed_control_type | DISCRETE |  | ✓
| cycling_degradation_coefficient | 0.1 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on A13: Data group containing performance information
Note on B14: Method used to control different speeds of the compressor
Note on B15: Cycling degradation coefficient (C~D~) as described in AHRI 210/240
Note on A16: Data group describing cooling performance over a range of conditions
Note on A17: Data group describing standby performance

## performance_map_cooling
performance.performance_map_cooling
grid_variables | [5 empty] | lookup_variables
outdoor_coil_entering_dry_bulb_temperature | indoor_coil_entering_relative_humidity | indoor_coil_entering_dry_bulb_temperature | indoor_coil_air_mass_flow_rate | compressor_sequence_number | ambient_absolute_air_pressure | gross_total_capacity | gross_sensible_capacity | gross_power | operation_state
K | - | K | kg/s | - | Pa | W | W | W | -
285.9278 | 0 | 291.4833 | 0.34644 | 1 | 57226.508 | 12209.5098 | 12869.6948 | 1446.1139 | NORMAL
285.9278 | 0 | 291.4833 | 0.34644 | 1 | 73773.932 | 11118.3477 | 11827.0274 | 1446.1139 | NORMAL
285.9278 | 0 | 291.4833 | 0.34644 | 1 | 90321.356 | 10414.6654 | 11130.3635 | 1446.1139 | NORMAL
285.9278 | 0 | 291.4833 | 0.34644 | 1 | 106868.78 | 9932.6614 | 10634.3238 | 1446.1139 | NORMAL
285.9278 | 0 | 291.4833 | 0.34644 | 2 | 57226.508 | 16564.2438 | 16842.3406 | 1948.1548 | NORMAL
285.9278 | 0 | 291.4833 | 0.34644 | 2 | 73773.932 | 15083.8998 | 15420.1058 | 1948.1548 | NORMAL
285.9278 | 0 | 291.4833 | 0.34644 | 2 | 90321.356 | 14129.2369 | 14493.0587 | 1948.1548 | NORMAL
285.9278 | 0 | 291.4833 | 0.34644 | 2 | 106868.78 | 13475.3178 | 13847.7001 | 1948.1548 | NORMAL
285.9278 | 0 | 291.4833 | 0.51403 | 1 | 57226.508 | 11709.213 | 13510.425 | 1489.7667 | NORMAL
285.9278 | 0 | 291.4833 | 0.51403 | 1 | 73773.932 | 10662.7624 | 12442.2137 | 1489.7667 | NORMAL
285.9278 | 0 | 291.4833 | 0.51403 | 1 | 90321.356 | 9987.9142 | 11701.4522 | 1489.7667 | NORMAL
285.9278 | 0 | 291.4833 | 0.51403 | 1 | 106868.78 | 9525.6608 | 11157.1797 | 1489.7667 | NORMAL
285.9278 | 0 | 291.4833 | 0.51403 | 2 | 57226.508 | 16883.8964 | 18032.7775 | 2212.6864 | NORMAL
285.9278 | 0 | 291.4833 | 0.51403 | 2 | 73773.932 | 15374.9852 | 16583.1965 | 2212.6864 | NORMAL
285.9278 | 0 | 291.4833 | 0.51403 | 2 | 90321.356 | 14401.8995 | 15607.7548 | 2212.6864 | NORMAL
285.9278 | 0 | 291.4833 | 0.51403 | 2 | 106868.78 | 13735.3612 | 14908.975 | 2212.6864 | NORMAL
285.9278 | 0 | 291.4833 | 0.68163 | 1 | 57226.508 | 11187.3757 | 14039.2557 | 1472.3925 | NORMAL
285.9278 | 0 | 291.4833 | 0.68163 | 1 | 73773.932 | 10187.5617 | 12922.9699 | 1472.3925 | NORMAL
285.9278 | 0 | 291.4833 | 0.68163 | 1 | 90321.356 | 9542.789 | 12132.8334 | 1472.3925 | NORMAL
285.9278 | 0 | 291.4833 | 0.68163 | 1 | 106868.78 | 9101.1365 | 11542.1804 | 1472.3925 | NORMAL
285.9278 | 0 | 291.4833 | 0.68163 | 2 | 57226.508 | 16346.09 | 18680.7253 | 2251.0175 | NORMAL
285.9278 | 0 | 291.4833 | 0.68163 | 2 | 73773.932 | 14885.2424 | 17203.1265 | 2251.0175 | NORMAL
285.9278 | 0 | 291.4833 | 0.68163 | 2 | 90321.356 | 13943.1526 | 16181.5054 | 2251.0175 | NORMAL
285.9278 | 0 | 291.4833 | 0.68163 | 2 | 106868.78 | 13297.8457 | 15432.7355 | 2251.0175 | NORMAL
285.9278 | 0 | 291.4833 | 0.84923 | 1 | 57226.508 | 10783.8998 | 14476.9427 | 1447.5907 | NORMAL
285.9278 | 0 | 291.4833 | 0.84923 | 1 | 73773.932 | 9820.1443 | 13313.4199 | 1447.5907 | NORMAL
285.9278 | 0 | 291.4833 | 0.84923 | 1 | 90321.356 | 9198.6256 | 12480.1562 | 1447.5907 | NORMAL
285.9278 | 0 | 291.4833 | 0.84923 | 1 | 106868.78 | 8772.9014 | 11851.0371 | 1447.5907 | NORMAL
285.9278 | 0 | 291.4833 | 0.84923 | 2 | 57226.508 | 15791.264 | 19259.205 | 2237.3378 | NORMAL
285.9278 | 0 | 291.4833 | 0.84923 | 2 | 73773.932 | 14380.0011 | 17732.8923 | 2237.3378 | NORMAL
285.9278 | 0 | 291.4833 | 0.84923 | 2 | 90321.356 | 13469.8881 | 16659.045 | 2237.3378 | NORMAL
285.9278 | 0 | 291.4833 | 0.84923 | 2 | 106868.78 | 12846.4845 | 15860.3996 | 2237.3378 | NORMAL
285.9278 | 0 | 296.113 | 0.34644 | 1 | 57226.508 | 11108.959 | 12333.5361 | 1446.1139 | NORMAL
285.9278 | 0 | 296.113 | 0.34644 | 1 | 73773.932 | 10148.8373 | 11401.0576 | 1446.1139 | NORMAL
285.9278 | 0 | 296.113 | 0.34644 | 1 | 90321.356 | 9561.0012 | 10784.1294 | 1446.1139 | NORMAL
285.9278 | 0 | 296.113 | 0.34644 | 1 | 106868.78 | 9183.0909 | 10352.2845 | 1446.1139 | NORMAL
285.9278 | 0 | 296.113 | 0.34644 | 2 | 57226.508 | 15071.1623 | 15708.843 | 1948.1548 | NORMAL
285.9278 | 0 | 296.113 | 0.34644 | 2 | 73773.932 | 13768.5966 | 14478.1974 | 1948.1548 | NORMAL
285.9278 | 0 | 296.113 | 0.34644 | 2 | 90321.356 | 12971.0985 | 13695.9034 | 1948.1548 | NORMAL
285.9278 | 0 | 296.113 | 0.34644 | 2 | 106868.78 | 12458.4 | 13168.5651 | 1948.1548 | NORMAL
285.9278 | 0 | 296.113 | 0.51403 | 1 | 57226.508 | 10653.7584 | 13456.6564 | 1489.7667 | NORMAL
285.9278 | 0 | 296.113 | 0.51403 | 1 | 73773.932 | 9732.9787 | 12443.3527 | 1489.7667 | NORMAL
285.9278 | 0 | 296.113 | 0.51403 | 1 | 90321.356 | 9169.2297 | 11741.0945 | 1489.7667 | NORMAL
285.9278 | 0 | 296.113 | 0.51403 | 1 | 106868.78 | 8806.8047 | 11228.141 | 1489.7667 | NORMAL
285.9278 | 0 | 296.113 | 0.51403 | 2 | 57226.508 | 15362.0019 | 17408.2251 | 2212.6864 | NORMAL
285.9278 | 0 | 296.113 | 0.51403 | 2 | 73773.932 | 14034.2996 | 16097.5962 | 2212.6864 | NORMAL
285.9278 | 0 | 296.113 | 0.51403 | 2 | 90321.356 | 13221.4115 | 15222.091 | 2212.6864 | NORMAL
285.9278 | 0 | 296.113 | 0.51403 | 2 | 106868.78 | 12698.8191 | 14603.7839 | 2212.6864 | NORMAL
285.9278 | 0 | 296.113 | 0.68163 | 1 | 57226.508 | 10178.9589 | 14306.5322 | 1472.3925 | NORMAL
285.9278 | 0 | 296.113 | 0.68163 | 1 | 73773.932 | 9299.215 | 13212.8835 | 1472.3925 | NORMAL
285.9278 | 0 | 296.113 | 0.68163 | 1 | 90321.356 | 8760.5903 | 12437.3451 | 1472.3925 | NORMAL
285.9278 | 0 | 296.113 | 0.68163 | 1 | 106868.78 | 8414.3172 | 11858.8166 | 1472.3925 | NORMAL
285.9278 | 0 | 296.113 | 0.68163 | 2 | 57226.508 | 14872.6727 | 18547.6089 | 2251.0175 | NORMAL
285.9278 | 0 | 296.113 | 0.68163 | 2 | 73773.932 | 13587.262 | 17152.6036 | 2251.0175 | NORMAL
285.9278 | 0 | 296.113 | 0.68163 | 2 | 90321.356 | 12800.267 | 16189.1174 | 2251.0175 | NORMAL
285.9278 | 0 | 296.113 | 0.68163 | 2 | 106868.78 | 12294.3209 | 15487.5571 | 2251.0175 | NORMAL
285.9278 | 0 | 296.113 | 0.84923 | 1 | 57226.508 | 9811.8518 | 14961.8943 | 1447.5907 | NORMAL
285.9278 | 0 | 296.113 | 0.84923 | 1 | 73773.932 | 8963.8362 | 13801.6592 | 1447.5907 | NORMAL
285.9278 | 0 | 296.113 | 0.84923 | 1 | 90321.356 | 8444.6371 | 12968.3888 | 1447.5907 | NORMAL
285.9278 | 0 | 296.113 | 0.84923 | 1 | 106868.78 | 8110.8525 | 12339.4878 | 1447.5907 | NORMAL
285.9278 | 0 | 296.113 | 0.84923 | 2 | 57226.508 | 14367.858 | 19489.9347 | 2237.3378 | NORMAL
285.9278 | 0 | 296.113 | 0.84923 | 2 | 73773.932 | 13126.0773 | 18008.5435 | 2237.3378 | NORMAL
285.9278 | 0 | 296.113 | 0.84923 | 2 | 90321.356 | 12365.7948 | 16965.0205 | 2237.3378 | NORMAL
285.9278 | 0 | 296.113 | 0.84923 | 2 | 106868.78 | 11877.0217 | 16191.3306 | 2237.3378 | NORMAL
285.9278 | 0 | 300.7426 | 0.34644 | 1 | 57226.508 | 10258.8428 | 12216.9735 | 1446.1139 | NORMAL
285.9278 | 0 | 300.7426 | 0.34644 | 1 | 73773.932 | 9447.761 | 11376.3593 | 1446.1139 | NORMAL
285.9278 | 0 | 300.7426 | 0.34644 | 1 | 90321.356 | 8992.358 | 10827.4247 | 1446.1139 | NORMAL
285.9278 | 0 | 300.7426 | 0.34644 | 1 | 106868.78 | 8734.1044 | 10452.6495 | 1446.1139 | NORMAL
285.9278 | 0 | 300.7426 | 0.34644 | 2 | 57226.508 | 13917.8375 | 15114.3914 | 1948.1548 | NORMAL
285.9278 | 0 | 300.7426 | 0.34644 | 2 | 73773.932 | 12817.4693 | 14061.8538 | 1948.1548 | NORMAL
285.9278 | 0 | 300.7426 | 0.34644 | 2 | 90321.356 | 12199.6389 | 13412.4829 | 1948.1548 | NORMAL
285.9278 | 0 | 300.7426 | 0.34644 | 2 | 106868.78 | 11849.2746 | 12995.398 | 1948.1548 | NORMAL
285.9278 | 0 | 300.7426 | 0.51403 | 1 | 57226.508 | 9838.4766 | 13793.585 | 1489.7667 | NORMAL
285.9278 | 0 | 300.7426 | 0.51403 | 1 | 73773.932 | 9060.6297 | 12822.8692 | 1489.7667 | NORMAL
285.9278 | 0 | 300.7426 | 0.51403 | 1 | 90321.356 | 8623.8873 | 12152.4297 | 1489.7667 | NORMAL
285.9278 | 0 | 300.7426 | 0.51403 | 1 | 106868.78 | 8376.2158 | 11667.4462 | 1489.7667 | NORMAL
285.9278 | 0 | 300.7426 | 0.51403 | 2 | 57226.508 | 14186.4205 | 17363.5133 | 2212.6864 | NORMAL
285.9278 | 0 | 300.7426 | 0.51403 | 2 | 73773.932 | 13064.8177 | 16166.6664 | 2212.6864 | NORMAL
285.9278 | 0 | 300.7426 | 0.51403 | 2 | 90321.356 | 12435.0645 | 15375.4899 | 2212.6864 | NORMAL
285.9278 | 0 | 300.7426 | 0.51403 | 2 | 106868.78 | 12077.939 | 14828.3713 | 2212.6864 | NORMAL
285.9278 | 0 | 300.7426 | 0.68163 | 1 | 57226.508 | 9400.0113 | 14937.3167 | 1472.3925 | NORMAL
285.9278 | 0 | 300.7426 | 0.68163 | 1 | 73773.932 | 8656.8302 | 13860.0015 | 1472.3925 | NORMAL
285.9278 | 0 | 300.7426 | 0.68163 | 1 | 90321.356 | 8239.5518 | 13096.4894 | 1472.3925 | NORMAL
285.9278 | 0 | 300.7426 | 0.68163 | 1 | 106868.78 | 8002.9182 | 12507.8196 | 1472.3925 | NORMAL
285.9278 | 0 | 300.7426 | 0.68163 | 2 | 57226.508 | 13734.5374 | 18962.005 | 2251.0175 | NORMAL
285.9278 | 0 | 300.7426 | 0.68163 | 2 | 73773.932 | 12648.6612 | 17631.3873 | 2251.0175 | NORMAL
285.9278 | 0 | 300.7426 | 0.68163 | 2 | 90321.356 | 12038.9677 | 16715.9822 | 2251.0175 | NORMAL
285.9278 | 0 | 300.7426 | 0.68163 | 2 | 106868.78 | 11693.2178 | 16056.4325 | 2251.0175 | NORMAL
285.9278 | 0 | 300.7426 | 0.84923 | 1 | 57226.508 | 9060.9972 | 15793.3488 | 1447.5907 | NORMAL
285.9278 | 0 | 300.7426 | 0.84923 | 1 | 73773.932 | 8344.6191 | 14633.731 | 1447.5907 | NORMAL
285.9278 | 0 | 300.7426 | 0.84923 | 1 | 90321.356 | 7942.39 | 13775.7895 | 1447.5907 | NORMAL
285.9278 | 0 | 300.7426 | 0.84923 | 1 | 106868.78 | 7714.2906 | 13112.8217 | 1447.5907 | NORMAL
285.9278 | 0 | 300.7426 | 0.84923 | 2 | 57226.508 | 13268.3538 | 20237.5935 | 2237.3378 | NORMAL
285.9278 | 0 | 300.7426 | 0.84923 | 2 | 73773.932 | 12219.3349 | 18789.7973 | 2237.3378 | NORMAL
285.9278 | 0 | 300.7426 | 0.84923 | 2 | 90321.356 | 11630.3358 | 17771.2865 | 2237.3378 | NORMAL
285.9278 | 0 | 300.7426 | 0.84923 | 2 | 106868.78 | 11296.3215 | 17012.8529 | 2237.3378 | NORMAL
285.9278 | 0 | 305.3722 | 0.34644 | 1 | 57226.508 | 9616.5058 | 12427.7424 | 1446.1139 | NORMAL
285.9278 | 0 | 305.3722 | 0.34644 | 1 | 73773.932 | 8968.8406 | 11660.303 | 1446.1139 | NORMAL
285.9278 | 0 | 305.3722 | 0.34644 | 1 | 90321.356 | 8658.9808 | 11167.7152 | 1446.1139 | NORMAL
285.9278 | 0 | 305.3722 | 0.34644 | 1 | 106868.78 | 8532.5005 | 10842.4931 | 1446.1139 | NORMAL
285.9278 | 0 | 305.3722 | 0.34644 | 2 | 57226.508 | 13046.3998 | 14974.4188 | 1948.1548 | NORMAL
285.9278 | 0 | 305.3722 | 0.34644 | 2 | 73773.932 | 12167.7335 | 14071.4907 | 1948.1548 | NORMAL
285.9278 | 0 | 305.3722 | 0.34644 | 2 | 90321.356 | 11747.3569 | 13535.6273 | 1948.1548 | NORMAL
285.9278 | 0 | 305.3722 | 0.34644 | 2 | 106868.78 | 11575.7651 | 13216.0048 | 1948.1548 | NORMAL
285.9278 | 0 | 305.3722 | 0.51403 | 1 | 57226.508 | 9222.4599 | 14425.1217 | 1489.7667 | NORMAL
285.9278 | 0 | 305.3722 | 0.51403 | 1 | 73773.932 | 8601.3335 | 13487.6445 | 1489.7667 | NORMAL
285.9278 | 0 | 305.3722 | 0.51403 | 1 | 90321.356 | 8304.1705 | 12830.3912 | 1489.7667 | NORMAL
285.9278 | 0 | 305.3722 | 0.51403 | 1 | 106868.78 | 8182.8728 | 12344.3603 | 1489.7667 | NORMAL
285.9278 | 0 | 305.3722 | 0.51403 | 2 | 57226.508 | 13298.166 | 17765.9722 | 2212.6864 | NORMAL
285.9278 | 0 | 305.3722 | 0.51403 | 2 | 73773.932 | 12402.5434 | 16659.2279 | 2212.6864 | NORMAL
285.9278 | 0 | 305.3722 | 0.51403 | 2 | 90321.356 | 11974.0545 | 15937.8147 | 2212.6864 | NORMAL
285.9278 | 0 | 305.3722 | 0.51403 | 2 | 106868.78 | 11799.1514 | 15452.5404 | 2212.6864 | NORMAL
285.9278 | 0 | 305.3722 | 0.68163 | 1 | 57226.508 | 8811.4482 | 15842.7039 | 1472.3925 | NORMAL
285.9278 | 0 | 305.3722 | 0.68163 | 1 | 73773.932 | 8218.0031 | 14752.9588 | 1472.3925 | NORMAL
285.9278 | 0 | 305.3722 | 0.68163 | 1 | 90321.356 | 7934.0836 | 13951.3496 | 1472.3925 | NORMAL
285.9278 | 0 | 305.3722 | 0.68163 | 1 | 106868.78 | 7818.1918 | 13363.4343 | 1472.3925 | NORMAL
285.9278 | 0 | 305.3722 | 0.68163 | 2 | 57226.508 | 12874.5766 | 19789.5661 | 2251.0175 | NORMAL
285.9278 | 0 | 305.3722 | 0.68163 | 2 | 73773.932 | 12007.4825 | 18509.2845 | 2251.0175 | NORMAL
285.9278 | 0 | 305.3722 | 0.68163 | 2 | 90321.356 | 11592.6423 | 17625.0906 | 2251.0175 | NORMAL
285.9278 | 0 | 305.3722 | 0.68163 | 2 | 106868.78 | 11423.3104 | 16967.8002 | 2251.0175 | NORMAL
285.9278 | 0 | 305.3722 | 0.84923 | 1 | 57226.508 | 8493.6608 | 16888.1869 | 1447.5907 | NORMAL
285.9278 | 0 | 305.3722 | 0.84923 | 1 | 73773.932 | 7921.6185 | 15663.5186 | 1447.5907 | NORMAL
285.9278 | 0 | 305.3722 | 0.84923 | 1 | 90321.356 | 7647.9387 | 14775.5131 | 1447.5907 | NORMAL
285.9278 | 0 | 305.3722 | 0.84923 | 1 | 106868.78 | 7536.2264 | 14113.6203 | 1447.5907 | NORMAL
285.9278 | 0 | 305.3722 | 0.84923 | 2 | 57226.508 | 12437.5821 | 21375.0698 | 2237.3378 | NORMAL
285.9278 | 0 | 305.3722 | 0.84923 | 2 | 73773.932 | 11599.9194 | 19942.6005 | 2237.3378 | NORMAL
285.9278 | 0 | 305.3722 | 0.84923 | 2 | 90321.356 | 11199.1598 | 18881.9222 | 2237.3378 | NORMAL
285.9278 | 0 | 305.3722 | 0.84923 | 2 | 106868.78 | 11035.5755 | 18110.7764 | 2237.3378 | NORMAL
285.9278 | 0.33333 | 291.4833 | 0.34644 | 1 | 57226.508 | 9090.24 | 6900.2552 | 1446.1139 | NORMAL
285.9278 | 0.33333 | 291.4833 | 0.34644 | 1 | 73773.932 | 8893.7548 | 7061.3669 | 1446.1139 | NORMAL
285.9278 | 0.33333 | 291.4833 | 0.34644 | 1 | 90321.356 | 8763.2891 | 7186.2929 | 1446.1139 | NORMAL
285.9278 | 0.33333 | 291.4833 | 0.34644 | 1 | 106868.78 | 8674.9115 | 7288.7555 | 1446.1139 | NORMAL
285.9278 | 0.33333 | 291.4833 | 0.34644 | 2 | 57226.508 | 12332.4321 | 8749.4724 | 1948.1548 | NORMAL
285.9278 | 0.33333 | 291.4833 | 0.34644 | 2 | 73773.932 | 12065.8672 | 9093.7024 | 1948.1548 | NORMAL
285.9278 | 0.33333 | 291.4833 | 0.34644 | 2 | 90321.356 | 11888.8685 | 9352.2243 | 1948.1548 | NORMAL
285.9278 | 0.33333 | 291.4833 | 0.34644 | 2 | 106868.78 | 11768.9695 | 9556.7692 | 1948.1548 | NORMAL
285.9278 | 0.33333 | 291.4833 | 0.51403 | 1 | 57226.508 | 8717.7584 | 7557.0689 | 1489.7667 | NORMAL
285.9278 | 0.33333 | 291.4833 | 0.51403 | 1 | 73773.932 | 8529.3244 | 7583.5078 | 1489.7667 | NORMAL
285.9278 | 0.33333 | 291.4833 | 0.51403 | 1 | 90321.356 | 8404.2046 | 7604.6549 | 1489.7667 | NORMAL
285.9278 | 0.33333 | 291.4833 | 0.51403 | 1 | 106868.78 | 8319.4484 | 7624.5415 | 1489.7667 | NORMAL
285.9278 | 0.33333 | 291.4833 | 0.51403 | 2 | 57226.508 | 12570.4204 | 9749.9973 | 2212.6864 | NORMAL
285.9278 | 0.33333 | 291.4833 | 0.51403 | 2 | 73773.932 | 12298.7113 | 9939.6945 | 2212.6864 | NORMAL
285.9278 | 0.33333 | 291.4833 | 0.51403 | 2 | 90321.356 | 12118.2969 | 10087.6172 | 2212.6864 | NORMAL
285.9278 | 0.33333 | 291.4833 | 0.51403 | 2 | 106868.78 | 11996.0842 | 10210.064 | 2212.6864 | NORMAL
285.9278 | 0.33333 | 291.4833 | 0.68163 | 1 | 57226.508 | 8329.2394 | 7984.6754 | 1472.3925 | NORMAL
285.9278 | 0.33333 | 291.4833 | 0.68163 | 1 | 73773.932 | 8149.2033 | 7922.8961 | 1472.3925 | NORMAL
285.9278 | 0.33333 | 291.4833 | 0.68163 | 1 | 90321.356 | 8029.6596 | 7874.0978 | 1472.3925 | NORMAL
285.9278 | 0.33333 | 291.4833 | 0.68163 | 1 | 106868.78 | 7948.6807 | 7836.9981 | 1472.3925 | NORMAL
285.9278 | 0.33333 | 291.4833 | 0.68163 | 2 | 57226.508 | 12170.012 | 10414.8867 | 2251.0175 | NORMAL
285.9278 | 0.33333 | 291.4833 | 0.68163 | 2 | 73773.932 | 11906.9578 | 10467.8894 | 2251.0175 | NORMAL
285.9278 | 0.33333 | 291.4833 | 0.68163 | 2 | 90321.356 | 11732.2902 | 10510.0815 | 2251.0175 | NORMAL
285.9278 | 0.33333 | 291.4833 | 0.68163 | 2 | 106868.78 | 11613.9703 | 10548.1142 | 2251.0175 | NORMAL
285.9278 | 0.33333 | 291.4833 | 0.84923 | 1 | 57226.508 | 8028.843 | 8301.7505 | 1447.5907 | NORMAL
285.9278 | 0.33333 | 291.4833 | 0.84923 | 1 | 73773.932 | 7855.2999 | 8176.3187 | 1447.5907 | NORMAL
285.9278 | 0.33333 | 291.4833 | 0.84923 | 1 | 90321.356 | 7740.0676 | 8077.0543 | 1447.5907 | NORMAL
285.9278 | 0.33333 | 291.4833 | 0.84923 | 1 | 106868.78 | 7662.0092 | 7998.629 | 1447.5907 | NORMAL
285.9278 | 0.33333 | 291.4833 | 0.84923 | 2 | 57226.508 | 11756.9322 | 10904.5954 | 2237.3378 | NORMAL
285.9278 | 0.33333 | 291.4833 | 0.84923 | 2 | 73773.932 | 11502.8066 | 10858.9728 | 2237.3378 | NORMAL
285.9278 | 0.33333 | 291.4833 | 0.84923 | 2 | 90321.356 | 11334.0677 | 10822.8733 | 2237.3378 | NORMAL
285.9278 | 0.33333 | 291.4833 | 0.84923 | 2 | 106868.78 | 11219.7639 | 10797.1483 | 2237.3378 | NORMAL
285.9278 | 0.33333 | 296.113 | 0.34644 | 1 | 57226.508 | 8560.3677 | 6587.4525 | 1446.1139 | NORMAL
285.9278 | 0.33333 | 296.113 | 0.34644 | 1 | 73773.932 | 8517.2589 | 6772.6939 | 1446.1139 | NORMAL
285.9278 | 0.33333 | 296.113 | 0.34644 | 1 | 90321.356 | 8511.5512 | 6939.6516 | 1446.1139 | NORMAL
285.9278 | 0.33333 | 296.113 | 0.34644 | 1 | 106868.78 | 8528.2868 | 7092.1672 | 1446.1139 | NORMAL
285.9278 | 0.33333 | 296.113 | 0.34644 | 2 | 57226.508 | 11613.5717 | 8096.8803 | 1948.1548 | NORMAL
285.9278 | 0.33333 | 296.113 | 0.34644 | 2 | 73773.932 | 11555.0873 | 8465.2482 | 1948.1548 | NORMAL
285.9278 | 0.33333 | 296.113 | 0.34644 | 2 | 90321.356 | 11547.344 | 8788.7519 | 1948.1548 | NORMAL
285.9278 | 0.33333 | 296.113 | 0.34644 | 2 | 106868.78 | 11570.0486 | 9076.228 | 1948.1548 | NORMAL
285.9278 | 0.33333 | 296.113 | 0.51403 | 1 | 57226.508 | 8209.5982 | 7407.0567 | 1489.7667 | NORMAL
285.9278 | 0.33333 | 296.113 | 0.51403 | 1 | 73773.932 | 8168.2557 | 7452.3596 | 1489.7667 | NORMAL
285.9278 | 0.33333 | 296.113 | 0.51403 | 1 | 90321.356 | 8162.782 | 7505.3785 | 1489.7667 | NORMAL
285.9278 | 0.33333 | 296.113 | 0.51403 | 1 | 106868.78 | 8178.8318 | 7563.1392 | 1489.7667 | NORMAL
285.9278 | 0.33333 | 296.113 | 0.51403 | 2 | 57226.508 | 11837.6875 | 9361.2971 | 2212.6864 | NORMAL
285.9278 | 0.33333 | 296.113 | 0.51403 | 2 | 73773.932 | 11778.0746 | 9582.9332 | 2212.6864 | NORMAL
285.9278 | 0.33333 | 296.113 | 0.51403 | 2 | 90321.356 | 11770.1818 | 9786.1087 | 2212.6864 | NORMAL
285.9278 | 0.33333 | 296.113 | 0.51403 | 2 | 106868.78 | 11793.3245 | 9974.3685 | 2212.6864 | NORMAL
285.9278 | 0.33333 | 296.113 | 0.68163 | 1 | 57226.508 | 7843.7261 | 7974.4136 | 1472.3925 | NORMAL
285.9278 | 0.33333 | 296.113 | 0.68163 | 1 | 73773.932 | 7804.2261 | 7925.6344 | 1472.3925 | NORMAL
285.9278 | 0.33333 | 296.113 | 0.68163 | 1 | 90321.356 | 7798.9963 | 7901.1224 | 1472.3925 | NORMAL
285.9278 | 0.33333 | 296.113 | 0.68163 | 1 | 106868.78 | 7814.3308 | 7893.421 | 1472.3925 | NORMAL
285.9278 | 0.33333 | 296.113 | 0.68163 | 2 | 57226.508 | 11460.6191 | 10188.8481 | 2251.0175 | NORMAL
285.9278 | 0.33333 | 296.113 | 0.68163 | 2 | 73773.932 | 11402.905 | 10268.6342 | 2251.0175 | NORMAL
285.9278 | 0.33333 | 296.113 | 0.68163 | 2 | 90321.356 | 11395.2636 | 10356.124 | 2251.0175 | NORMAL
285.9278 | 0.33333 | 296.113 | 0.68163 | 2 | 106868.78 | 11417.6692 | 10447.9912 | 2251.0175 | NORMAL
285.9278 | 0.33333 | 296.113 | 0.84923 | 1 | 57226.508 | 7560.8398 | 8391.8231 | 1447.5907 | NORMAL
285.9278 | 0.33333 | 296.113 | 0.84923 | 1 | 73773.932 | 7522.7645 | 8277.407 | 1447.5907 | NORMAL
285.9278 | 0.33333 | 296.113 | 0.84923 | 1 | 90321.356 | 7517.7233 | 8198.6494 | 1447.5907 | NORMAL
285.9278 | 0.33333 | 296.113 | 0.84923 | 1 | 106868.78 | 7532.5048 | 8144.9538 | 1447.5907 | NORMAL
285.9278 | 0.33333 | 296.113 | 0.84923 | 2 | 57226.508 | 11071.6178 | 10825.8558 | 2237.3378 | NORMAL
285.9278 | 0.33333 | 296.113 | 0.84923 | 2 | 73773.932 | 11015.8627 | 10799.7496 | 2237.3378 | NORMAL
285.9278 | 0.33333 | 296.113 | 0.84923 | 2 | 90321.356 | 11008.4807 | 10800.0884 | 2237.3378 | NORMAL
285.9278 | 0.33333 | 296.113 | 0.84923 | 2 | 106868.78 | 11030.1257 | 10818.4966 | 2237.3378 | NORMAL
285.9278 | 0.33333 | 300.7426 | 0.34644 | 1 | 57226.508 | 8611.389 | 6547.4353 | 1467.663 | NORMAL
285.9278 | 0.33333 | 300.7426 | 0.34644 | 1 | 73773.932 | 8716.7087 | 6764.3141 | 1483.1556 | NORMAL
285.9278 | 0.33333 | 300.7426 | 0.34644 | 1 | 90321.356 | 8835.252 | 6980.4403 | 1494.0893 | NORMAL
285.9278 | 0.33333 | 300.7426 | 0.34644 | 1 | 106868.78 | 8959.2222 | 7191.3781 | 1501.6755 | NORMAL
285.9278 | 0.33333 | 300.7426 | 0.34644 | 2 | 57226.508 | 11682.7907 | 7887.992 | 1977.1851 | NORMAL
285.9278 | 0.33333 | 300.7426 | 0.34644 | 2 | 73773.932 | 11825.6745 | 8327.4539 | 1998.0562 | NORMAL
285.9278 | 0.33333 | 300.7426 | 0.34644 | 2 | 90321.356 | 11986.4982 | 8744.2557 | 2012.7857 | NORMAL
285.9278 | 0.33333 | 300.7426 | 0.34644 | 2 | 106868.78 | 12154.6846 | 9135.8221 | 2023.0056 | NORMAL
285.9278 | 0.33333 | 300.7426 | 0.51403 | 1 | 57226.508 | 8258.5288 | 7544.991 | 1511.9663 | NORMAL
285.9278 | 0.33333 | 300.7426 | 0.51403 | 1 | 73773.932 | 8359.533 | 7616.8971 | 1527.9266 | NORMAL
285.9278 | 0.33333 | 300.7426 | 0.51403 | 1 | 90321.356 | 8473.2188 | 7708.6421 | 1539.1903 | NORMAL
285.9278 | 0.33333 | 300.7426 | 0.51403 | 1 | 106868.78 | 8592.1092 | 7811.3127 | 1547.0056 | NORMAL
285.9278 | 0.33333 | 300.7426 | 0.51403 | 2 | 57226.508 | 11908.2423 | 9351.6081 | 2245.6586 | NORMAL
285.9278 | 0.33333 | 300.7426 | 0.51403 | 2 | 73773.932 | 12053.8834 | 9615.608 | 2269.3637 | NORMAL
285.9278 | 0.33333 | 300.7426 | 0.51403 | 2 | 90321.356 | 12217.8107 | 9883.8912 | 2286.0932 | NORMAL
285.9278 | 0.33333 | 300.7426 | 0.51403 | 2 | 106868.78 | 12389.2427 | 10149.2486 | 2297.7009 | NORMAL
285.9278 | 0.33333 | 300.7426 | 0.68163 | 1 | 57226.508 | 7890.4761 | 8230.8006 | 1494.3333 | NORMAL
285.9278 | 0.33333 | 300.7426 | 0.68163 | 1 | 73773.932 | 7986.9788 | 8206.2219 | 1510.1074 | NORMAL
285.9278 | 0.33333 | 300.7426 | 0.68163 | 1 | 90321.356 | 8095.598 | 8215.3146 | 1521.2398 | NORMAL
285.9278 | 0.33333 | 300.7426 | 0.68163 | 1 | 106868.78 | 8209.19 | 8245.7461 | 1528.9639 | NORMAL
285.9278 | 0.33333 | 300.7426 | 0.68163 | 2 | 57226.508 | 11528.9264 | 10359.1732 | 2284.5608 | NORMAL
285.9278 | 0.33333 | 300.7426 | 0.68163 | 2 | 73773.932 | 11669.9284 | 10476.397 | 2308.6766 | NORMAL
285.9278 | 0.33333 | 300.7426 | 0.68163 | 2 | 90321.356 | 11828.6341 | 10618.7109 | 2325.6959 | NORMAL
285.9278 | 0.33333 | 300.7426 | 0.68163 | 2 | 106868.78 | 11994.6055 | 10774.3188 | 2337.5047 | NORMAL
285.9278 | 0.33333 | 300.7426 | 0.84923 | 1 | 57226.508 | 7605.9038 | 8731.019 | 1469.1618 | NORMAL
285.9278 | 0.33333 | 300.7426 | 0.84923 | 1 | 73773.932 | 7698.9261 | 8639.3784 | 1484.6702 | NORMAL
285.9278 | 0.33333 | 300.7426 | 0.84923 | 1 | 90321.356 | 7803.628 | 8591.1927 | 1495.6151 | NORMAL
285.9278 | 0.33333 | 300.7426 | 0.84923 | 1 | 106868.78 | 7913.1232 | 8571.5967 | 1503.2091 | NORMAL
285.9278 | 0.33333 | 300.7426 | 0.84923 | 2 | 57226.508 | 11137.6066 | 11129.6704 | 2270.6773 | NORMAL
285.9278 | 0.33333 | 300.7426 | 0.84923 | 2 | 73773.932 | 11273.8227 | 11138.1864 | 2294.6465 | NORMAL
285.9278 | 0.33333 | 300.7426 | 0.84923 | 2 | 90321.356 | 11427.1415 | 11187.3379 | 2311.5624 | NORMAL
285.9278 | 0.33333 | 300.7426 | 0.84923 | 2 | 106868.78 | 11587.4794 | 11261.5423 | 2323.2994 | NORMAL
285.9278 | 0.33333 | 305.3722 | 0.34644 | 1 | 57226.508 | 9257.2267 | 6729.2775 | 1510.3903 | NORMAL
285.9278 | 0.33333 | 305.3722 | 0.34644 | 1 | 73773.932 | 9499.3424 | 6987.0309 | 1510.63 | NORMAL
285.9278 | 0.33333 | 305.3722 | 0.34644 | 1 | 90321.356 | 9735.5152 | 7260.246 | 1506.2552 | NORMAL
285.9278 | 0.33333 | 305.3722 | 0.34644 | 1 | 106868.78 | 9963.1812 | 7538.1199 | 1498.2404 | NORMAL
285.9278 | 0.33333 | 305.3722 | 0.34644 | 2 | 57226.508 | 12558.9776 | 7987.996 | 2034.7458 | NORMAL
285.9278 | 0.33333 | 305.3722 | 0.34644 | 2 | 73773.932 | 12887.4481 | 8491.0422 | 2035.0688 | NORMAL
285.9278 | 0.33333 | 305.3722 | 0.34644 | 2 | 90321.356 | 13207.856 | 9000.9309 | 2029.1752 | NORMAL
285.9278 | 0.33333 | 305.3722 | 0.34644 | 2 | 106868.78 | 13516.723 | 9503.8462 | 2018.3779 | NORMAL
285.9278 | 0.33333 | 305.3722 | 0.51403 | 1 | 57226.508 | 8877.9027 | 7876.2817 | 1555.9834 | NORMAL
285.9278 | 0.33333 | 305.3722 | 0.51403 | 1 | 73773.932 | 9110.0975 | 7983.6596 | 1556.2304 | NORMAL
285.9278 | 0.33333 | 305.3722 | 0.51403 | 1 | 90321.356 | 9336.5928 | 8122.286 | 1551.7235 | NORMAL
285.9278 | 0.33333 | 305.3722 | 0.51403 | 1 | 106868.78 | 9554.93 | 8278.228 | 1543.4667 | NORMAL
285.9278 | 0.33333 | 305.3722 | 0.51403 | 2 | 57226.508 | 12801.3376 | 9642.3416 | 2311.0353 | NORMAL
285.9278 | 0.33333 | 305.3722 | 0.51403 | 2 | 73773.932 | 13136.1469 | 9961.5231 | 2311.4021 | NORMAL
285.9278 | 0.33333 | 305.3722 | 0.51403 | 2 | 90321.356 | 13462.7379 | 10306.0323 | 2304.7082 | NORMAL
285.9278 | 0.33333 | 305.3722 | 0.51403 | 2 | 106868.78 | 13777.5654 | 10660.2537 | 2292.4447 | NORMAL
285.9278 | 0.33333 | 305.3722 | 0.68163 | 1 | 57226.508 | 8482.2467 | 8663.8528 | 1537.837 | NORMAL
285.9278 | 0.33333 | 305.3722 | 0.68163 | 1 | 73773.932 | 8704.0934 | 8671.9173 | 1538.0811 | NORMAL
285.9278 | 0.33333 | 305.3722 | 0.68163 | 1 | 90321.356 | 8920.4946 | 8722.7963 | 1533.6268 | NORMAL
285.9278 | 0.33333 | 305.3722 | 0.68163 | 1 | 106868.78 | 9129.1013 | 8799.7272 | 1525.4663 | NORMAL
285.9278 | 0.33333 | 305.3722 | 0.68163 | 2 | 57226.508 | 12393.5738 | 10801.2479 | 2351.07 | NORMAL
285.9278 | 0.33333 | 305.3722 | 0.68163 | 2 | 73773.932 | 12717.7183 | 10968.299 | 2351.4432 | NORMAL
285.9278 | 0.33333 | 305.3722 | 0.68163 | 2 | 90321.356 | 13033.9064 | 11176.7558 | 2344.6333 | NORMAL
285.9278 | 0.33333 | 305.3722 | 0.68163 | 2 | 106868.78 | 13338.7056 | 11407.7257 | 2332.1575 | NORMAL
285.9278 | 0.33333 | 305.3722 | 0.84923 | 1 | 57226.508 | 8176.332 | 9236.3768 | 1511.9327 | NORMAL
285.9278 | 0.33333 | 305.3722 | 0.84923 | 1 | 73773.932 | 8390.1778 | 9175.6634 | 1512.1727 | NORMAL
285.9278 | 0.33333 | 305.3722 | 0.84923 | 1 | 90321.356 | 8598.7744 | 9166.2542 | 1507.7934 | NORMAL
285.9278 | 0.33333 | 305.3722 | 0.84923 | 1 | 106868.78 | 8799.8576 | 9189.1814 | 1499.7704 | NORMAL
285.9278 | 0.33333 | 305.3722 | 0.84923 | 2 | 57226.508 | 11972.9058 | 11686.0952 | 2336.7823 | NORMAL
285.9278 | 0.33333 | 305.3722 | 0.84923 | 2 | 73773.932 | 12286.0481 | 11741.1569 | 2337.1532 | NORMAL
285.9278 | 0.33333 | 305.3722 | 0.84923 | 2 | 90321.356 | 12591.5039 | 11850.4816 | 2330.3847 | NORMAL
285.9278 | 0.33333 | 305.3722 | 0.84923 | 2 | 106868.78 | 12885.9575 | 11992.0931 | 2317.9847 | NORMAL
285.9278 | 0.66667 | 291.4833 | 0.34644 | 1 | 57226.508 | 8528.8059 | 4068.8902 | 1446.1139 | NORMAL
285.9278 | 0.66667 | 291.4833 | 0.34644 | 1 | 73773.932 | 8545.6603 | 4515.0107 | 1450.4657 | NORMAL
285.9278 | 0.66667 | 291.4833 | 0.34644 | 1 | 90321.356 | 8564.3777 | 4903.4649 | 1456.6233 | NORMAL
285.9278 | 0.66667 | 291.4833 | 0.34644 | 1 | 106868.78 | 8583.9281 | 5240.0552 | 1461.7648 | NORMAL
285.9278 | 0.66667 | 291.4833 | 0.34644 | 2 | 57226.508 | 11570.7528 | 5286.9555 | 1948.1548 | NORMAL
285.9278 | 0.66667 | 291.4833 | 0.34644 | 2 | 73773.932 | 11593.6186 | 5989.6036 | 1954.0174 | NORMAL
285.9278 | 0.66667 | 291.4833 | 0.34644 | 2 | 90321.356 | 11619.0119 | 6571.6278 | 1962.3128 | NORMAL
285.9278 | 0.66667 | 291.4833 | 0.34644 | 2 | 106868.78 | 11645.5353 | 7068.7687 | 1969.2393 | NORMAL
285.9278 | 0.66667 | 291.4833 | 0.51403 | 1 | 57226.508 | 8179.3296 | 4281.7636 | 1489.7667 | NORMAL
285.9278 | 0.66667 | 291.4833 | 0.51403 | 1 | 73773.932 | 8195.4934 | 4631.6076 | 1494.2499 | NORMAL
285.9278 | 0.66667 | 291.4833 | 0.51403 | 1 | 90321.356 | 8213.4438 | 4939.4113 | 1500.5933 | NORMAL
285.9278 | 0.66667 | 291.4833 | 0.51403 | 1 | 106868.78 | 8232.1932 | 5209.1694 | 1505.8901 | NORMAL
285.9278 | 0.66667 | 291.4833 | 0.51403 | 2 | 57226.508 | 11794.0423 | 5709.2069 | 2212.6864 | NORMAL
285.9278 | 0.66667 | 291.4833 | 0.51403 | 2 | 73773.932 | 11817.3494 | 6304.0451 | 2219.3451 | NORMAL
285.9278 | 0.66667 | 291.4833 | 0.51403 | 2 | 90321.356 | 11843.2327 | 6823.0727 | 2228.7668 | NORMAL
285.9278 | 0.66667 | 291.4833 | 0.51403 | 2 | 106868.78 | 11870.268 | 7273.9516 | 2236.6339 | NORMAL
285.9278 | 0.66667 | 291.4833 | 0.68163 | 1 | 57226.508 | 7814.8065 | 4425.6718 | 1472.3925 | NORMAL
285.9278 | 0.66667 | 291.4833 | 0.68163 | 1 | 73773.932 | 7830.2499 | 4712.9055 | 1476.8234 | NORMAL
285.9278 | 0.66667 | 291.4833 | 0.68163 | 1 | 90321.356 | 7847.4003 | 4967.5707 | 1483.0929 | NORMAL
285.9278 | 0.66667 | 291.4833 | 0.68163 | 1 | 106868.78 | 7865.3141 | 5192.1404 | 1488.3279 | NORMAL
285.9278 | 0.66667 | 291.4833 | 0.68163 | 2 | 57226.508 | 11418.3641 | 5922.1762 | 2251.0175 | NORMAL
285.9278 | 0.66667 | 291.4833 | 0.68163 | 2 | 73773.932 | 11440.9288 | 6419.5086 | 2257.7915 | NORMAL
285.9278 | 0.66667 | 291.4833 | 0.68163 | 2 | 90321.356 | 11465.9876 | 6856.6902 | 2267.3764 | NORMAL
285.9278 | 0.66667 | 291.4833 | 0.68163 | 2 | 106868.78 | 11492.1618 | 7239.52 | 2275.3798 | NORMAL
285.9278 | 0.66667 | 291.4833 | 0.84923 | 1 | 57226.508 | 7532.9632 | 4535.3199 | 1447.5907 | NORMAL
285.9278 | 0.66667 | 291.4833 | 0.84923 | 1 | 73773.932 | 7547.8497 | 4780.1773 | 1451.9469 | NORMAL
285.9278 | 0.66667 | 291.4833 | 0.84923 | 1 | 90321.356 | 7564.3816 | 4998.79 | 1458.1108 | NORMAL
285.9278 | 0.66667 | 291.4833 | 0.84923 | 1 | 106868.78 | 7581.6493 | 5192.4635 | 1463.2576 | NORMAL
285.9278 | 0.66667 | 291.4833 | 0.84923 | 2 | 57226.508 | 11030.7971 | 6084.7025 | 2237.3378 | NORMAL
285.9278 | 0.66667 | 291.4833 | 0.84923 | 2 | 73773.932 | 11052.5959 | 6511.2905 | 2244.0706 | NORMAL
285.9278 | 0.66667 | 291.4833 | 0.84923 | 2 | 90321.356 | 11076.8041 | 6888.5034 | 2253.5973 | NORMAL
285.9278 | 0.66667 | 291.4833 | 0.84923 | 2 | 106868.78 | 11102.0898 | 7220.4827 | 2261.552 | NORMAL
285.9278 | 0.66667 | 296.113 | 0.34644 | 1 | 57226.508 | 9141.6044 | 3903.7436 | 1508.2904 | NORMAL
285.9278 | 0.66667 | 296.113 | 0.34644 | 1 | 73773.932 | 9221.504 | 4354.16 | 1509.8926 | NORMAL
285.9278 | 0.66667 | 296.113 | 0.34644 | 1 | 90321.356 | 9295.4046 | 4770.4528 | 1510.7819 | NORMAL
285.9278 | 0.66667 | 296.113 | 0.34644 | 1 | 106868.78 | 9363.8498 | 5150.7511 | 1511.1389 | NORMAL
285.9278 | 0.66667 | 296.113 | 0.34644 | 2 | 57226.508 | 12402.1166 | 4975.0377 | 2031.9169 | NORMAL
285.9278 | 0.66667 | 296.113 | 0.34644 | 2 | 73773.932 | 12510.5138 | 5686.7559 | 2034.0753 | NORMAL
285.9278 | 0.66667 | 296.113 | 0.34644 | 2 | 90321.356 | 12610.7723 | 6342.2342 | 2035.2734 | NORMAL
285.9278 | 0.66667 | 296.113 | 0.34644 | 2 | 106868.78 | 12703.6296 | 6936.2532 | 2035.7544 | NORMAL
285.9278 | 0.66667 | 296.113 | 0.51403 | 1 | 57226.508 | 8767.0181 | 4203.5914 | 1553.8201 | NORMAL
285.9278 | 0.66667 | 296.113 | 0.51403 | 1 | 73773.932 | 8843.6438 | 4557.1907 | 1555.4707 | NORMAL
285.9278 | 0.66667 | 296.113 | 0.51403 | 1 | 90321.356 | 8914.5162 | 4886.2093 | 1556.3869 | NORMAL
285.9278 | 0.66667 | 296.113 | 0.51403 | 1 | 106868.78 | 8980.1568 | 5189.0784 | 1556.7546 | NORMAL
285.9278 | 0.66667 | 296.113 | 0.51403 | 2 | 57226.508 | 12641.4496 | 5502.2271 | 2307.8222 | NORMAL
285.9278 | 0.66667 | 296.113 | 0.51403 | 2 | 73773.932 | 12751.9386 | 6102.7087 | 2310.2737 | NORMAL
285.9278 | 0.66667 | 296.113 | 0.51403 | 2 | 90321.356 | 12854.1319 | 6658.2123 | 2311.6345 | NORMAL
285.9278 | 0.66667 | 296.113 | 0.51403 | 2 | 106868.78 | 12948.7811 | 7166.4315 | 2312.1807 | NORMAL
285.9278 | 0.66667 | 296.113 | 0.68163 | 1 | 57226.508 | 8376.3038 | 4405.0052 | 1535.699 | NORMAL
285.9278 | 0.66667 | 296.113 | 0.68163 | 1 | 73773.932 | 8449.5145 | 4696.1564 | 1537.3303 | NORMAL
285.9278 | 0.66667 | 296.113 | 0.68163 | 1 | 90321.356 | 8517.2285 | 4969.3209 | 1538.2358 | NORMAL
285.9278 | 0.66667 | 296.113 | 0.68163 | 1 | 106868.78 | 8579.9436 | 5222.3299 | 1538.5992 | NORMAL
285.9278 | 0.66667 | 296.113 | 0.68163 | 2 | 57226.508 | 12238.7787 | 5803.226 | 2347.8014 | NORMAL
285.9278 | 0.66667 | 296.113 | 0.68163 | 2 | 73773.932 | 12345.7483 | 6305.7704 | 2350.2953 | NORMAL
285.9278 | 0.66667 | 296.113 | 0.68163 | 2 | 90321.356 | 12444.6864 | 6773.0084 | 2351.6797 | NORMAL
285.9278 | 0.66667 | 296.113 | 0.68163 | 2 | 106868.78 | 12536.3208 | 7202.818 | 2352.2354 | NORMAL
285.9278 | 0.66667 | 296.113 | 0.84923 | 1 | 57226.508 | 8074.21 | 4554.4235 | 1509.8307 | NORMAL
285.9278 | 0.66667 | 296.113 | 0.84923 | 1 | 73773.932 | 8144.7804 | 4803.3982 | 1511.4345 | NORMAL
285.9278 | 0.66667 | 296.113 | 0.84923 | 1 | 90321.356 | 8210.0522 | 5039.0655 | 1512.3248 | NORMAL
285.9278 | 0.66667 | 296.113 | 0.84923 | 1 | 106868.78 | 8270.5055 | 5258.6108 | 1512.6821 | NORMAL
285.9278 | 0.66667 | 296.113 | 0.84923 | 2 | 57226.508 | 11823.3648 | 6030.5992 | 2333.5335 | NORMAL
285.9278 | 0.66667 | 296.113 | 0.84923 | 2 | 73773.932 | 11926.7036 | 6462.5303 | 2336.0123 | NORMAL
285.9278 | 0.66667 | 296.113 | 0.84923 | 2 | 90321.356 | 12022.2835 | 6866.5211 | 2337.3882 | NORMAL
285.9278 | 0.66667 | 296.113 | 0.84923 | 2 | 106868.78 | 12110.8076 | 7239.89 | 2337.9406 | NORMAL
285.9278 | 0.66667 | 300.7426 | 0.34644 | 1 | 57226.508 | 10631.8801 | 3957.5657 | 1455.3551 | NORMAL
285.9278 | 0.66667 | 300.7426 | 0.34644 | 1 | 73773.932 | 10765.0681 | 4443.3971 | 1450.5616 | NORMAL
285.9278 | 0.66667 | 300.7426 | 0.34644 | 1 | 90321.356 | 10886.9953 | 4914.3946 | 1450.5616 | NORMAL
285.9278 | 0.66667 | 300.7426 | 0.34644 | 1 | 106868.78 | 10999.7631 | 5362.422 | 1450.5616 | NORMAL
285.9278 | 0.66667 | 300.7426 | 0.34644 | 2 | 57226.508 | 14423.9251 | 4989.0745 | 1960.6043 | NORMAL
285.9278 | 0.66667 | 300.7426 | 0.34644 | 2 | 73773.932 | 14604.6169 | 5758.3978 | 1954.1467 | NORMAL
285.9278 | 0.66667 | 300.7426 | 0.34644 | 2 | 90321.356 | 14770.0315 | 6505.9683 | 1954.1467 | NORMAL
285.9278 | 0.66667 | 300.7426 | 0.34644 | 2 | 106868.78 | 14923.0198 | 7215.8181 | 1954.1467 | NORMAL
285.9278 | 0.66667 | 300.7426 | 0.51403 | 1 | 57226.508 | 10196.2283 | 4318.4182 | 1499.2869 | NORMAL
285.9278 | 0.66667 | 300.7426 | 0.51403 | 1 | 73773.932 | 10323.9588 | 4701.4927 | 1494.3487 | NORMAL
285.9278 | 0.66667 | 300.7426 | 0.51403 | 1 | 90321.356 | 10440.8899 | 5074.4446 | 1494.3487 | NORMAL
285.9278 | 0.66667 | 300.7426 | 0.51403 | 1 | 106868.78 | 10549.0369 | 5430.3145 | 1494.3487 | NORMAL
285.9278 | 0.66667 | 300.7426 | 0.51403 | 2 | 57226.508 | 14702.2744 | 5592.483 | 2226.8264 | NORMAL
285.9278 | 0.66667 | 300.7426 | 0.51403 | 2 | 73773.932 | 14886.4531 | 6240.3426 | 2219.4919 | NORMAL
285.9278 | 0.66667 | 300.7426 | 0.51403 | 2 | 90321.356 | 15055.0599 | 6868.4735 | 2219.4919 | NORMAL
285.9278 | 0.66667 | 300.7426 | 0.51403 | 2 | 106868.78 | 15211.0006 | 7466.1854 | 2219.4919 | NORMAL
285.9278 | 0.66667 | 300.7426 | 0.68163 | 1 | 57226.508 | 9741.8193 | 4561.5689 | 1481.8017 | NORMAL
285.9278 | 0.66667 | 300.7426 | 0.68163 | 1 | 73773.932 | 9863.8573 | 4879.3009 | 1476.9211 | NORMAL
285.9278 | 0.66667 | 300.7426 | 0.68163 | 1 | 90321.356 | 9975.5772 | 5191.4202 | 1476.9211 | NORMAL
285.9278 | 0.66667 | 300.7426 | 0.68163 | 1 | 106868.78 | 10078.9045 | 5490.6473 | 1476.9211 | NORMAL
285.9278 | 0.66667 | 300.7426 | 0.68163 | 2 | 57226.508 | 14233.9596 | 5955.3097 | 2265.4024 | NORMAL
285.9278 | 0.66667 | 300.7426 | 0.68163 | 2 | 73773.932 | 14412.2717 | 6499.3819 | 2257.9409 | NORMAL
285.9278 | 0.66667 | 300.7426 | 0.68163 | 2 | 90321.356 | 14575.5078 | 7028.6763 | 2257.9409 | NORMAL
285.9278 | 0.66667 | 300.7426 | 0.68163 | 2 | 106868.78 | 14726.4813 | 7533.5161 | 2257.9409 | NORMAL
285.9278 | 0.66667 | 300.7426 | 0.84923 | 1 | 57226.508 | 9390.4778 | 4740.6392 | 1456.8413 | NORMAL
285.9278 | 0.66667 | 300.7426 | 0.84923 | 1 | 73773.932 | 9508.1144 | 5014.5038 | 1452.043 | NORMAL
285.9278 | 0.66667 | 300.7426 | 0.84923 | 1 | 90321.356 | 9615.8052 | 5286.3194 | 1452.043 | NORMAL
285.9278 | 0.66667 | 300.7426 | 0.84923 | 1 | 106868.78 | 9715.4059 | 5548.2775 | 1452.043 | NORMAL
285.9278 | 0.66667 | 300.7426 | 0.84923 | 2 | 57226.508 | 13750.8244 | 6229.5562 | 2251.6353 | NORMAL
285.9278 | 0.66667 | 300.7426 | 0.84923 | 2 | 73773.932 | 13923.0842 | 6699.6152 | 2244.2191 | NORMAL
285.9278 | 0.66667 | 300.7426 | 0.84923 | 2 | 90321.356 | 14080.7797 | 7159.7552 | 2244.2191 | NORMAL
285.9278 | 0.66667 | 300.7426 | 0.84923 | 2 | 106868.78 | 14226.6287 | 7600.0915 | 2244.2191 | NORMAL
285.9278 | 0.66667 | 305.3722 | 0.34644 | 1 | 57226.508 | 13012.5395 | 4125.2131 | 1450.5616 | NORMAL
285.9278 | 0.66667 | 305.3722 | 0.34644 | 1 | 73773.932 | 13187.8581 | 4665.9127 | 1450.5616 | NORMAL
285.9278 | 0.66667 | 305.3722 | 0.34644 | 1 | 90321.356 | 13349.8744 | 5210.7987 | 1450.5616 | NORMAL
285.9278 | 0.66667 | 305.3722 | 0.34644 | 1 | 106868.78 | 13500.1588 | 5747.627 | 1450.5616 | NORMAL
285.9278 | 0.66667 | 305.3722 | 0.34644 | 2 | 57226.508 | 17653.688 | 5169.9925 | 1954.1467 | NORMAL
285.9278 | 0.66667 | 305.3722 | 0.34644 | 2 | 73773.932 | 17891.537 | 6029.9882 | 1954.1467 | NORMAL
285.9278 | 0.66667 | 305.3722 | 0.34644 | 2 | 90321.356 | 18111.3392 | 6904.3016 | 1954.1467 | NORMAL
285.9278 | 0.66667 | 305.3722 | 0.34644 | 2 | 106868.78 | 18315.2252 | 7769.9061 | 1954.1467 | NORMAL
285.9278 | 0.66667 | 305.3722 | 0.51403 | 1 | 57226.508 | 12479.3378 | 4535.6814 | 1494.3487 | NORMAL
285.9278 | 0.66667 | 305.3722 | 0.51403 | 1 | 73773.932 | 12647.4725 | 4963.0301 | 1494.3487 | NORMAL
285.9278 | 0.66667 | 305.3722 | 0.51403 | 1 | 90321.356 | 12802.85 | 5393.998 | 1494.3487 | NORMAL
285.9278 | 0.66667 | 305.3722 | 0.51403 | 1 | 106868.78 | 12946.9764 | 5818.0064 | 1494.3487 | NORMAL
285.9278 | 0.66667 | 305.3722 | 0.51403 | 2 | 57226.508 | 17994.3645 | 5837.8447 | 2219.4919 | NORMAL
285.9278 | 0.66667 | 305.3722 | 0.51403 | 2 | 73773.932 | 18236.8034 | 6558.7348 | 2219.4919 | NORMAL
285.9278 | 0.66667 | 305.3722 | 0.51403 | 2 | 90321.356 | 18460.8473 | 7284.5432 | 2219.4919 | NORMAL
285.9278 | 0.66667 | 305.3722 | 0.51403 | 2 | 106868.78 | 18668.6679 | 7999.056 | 2219.4919 | NORMAL
285.9278 | 0.66667 | 305.3722 | 0.68163 | 1 | 57226.508 | 11923.1788 | 4813.5469 | 1476.9211 | NORMAL
285.9278 | 0.66667 | 305.3722 | 0.68163 | 1 | 73773.932 | 12083.8204 | 5170.2271 | 1476.9211 | NORMAL
285.9278 | 0.66667 | 305.3722 | 0.68163 | 1 | 90321.356 | 12232.2733 | 5533.0154 | 1476.9211 | NORMAL
285.9278 | 0.66667 | 305.3722 | 0.68163 | 1 | 106868.78 | 12369.9765 | 5891.1647 | 1476.9211 | NORMAL
285.9278 | 0.66667 | 305.3722 | 0.68163 | 2 | 57226.508 | 17421.1861 | 6250.9879 | 2257.9409 | NORMAL
285.9278 | 0.66667 | 305.3722 | 0.68163 | 2 | 73773.932 | 17655.9026 | 6857.624 | 2257.9409 | NORMAL
285.9278 | 0.66667 | 305.3722 | 0.68163 | 2 | 90321.356 | 17872.8099 | 7469.025 | 2257.9409 | NORMAL
285.9278 | 0.66667 | 305.3722 | 0.68163 | 2 | 106868.78 | 18074.0107 | 8070.4497 | 2257.9409 | NORMAL
285.9278 | 0.66667 | 305.3722 | 0.84923 | 1 | 57226.508 | 11493.166 | 5017.7507 | 1452.043 | NORMAL
285.9278 | 0.66667 | 305.3722 | 0.84923 | 1 | 73773.932 | 11648.014 | 5327.3942 | 1452.043 | NORMAL
285.9278 | 0.66667 | 305.3722 | 0.84923 | 1 | 90321.356 | 11791.1129 | 5645.7155 | 1452.043 | NORMAL
285.9278 | 0.66667 | 305.3722 | 0.84923 | 1 | 106868.78 | 11923.8498 | 5961.5001 | 1452.043 | NORMAL
285.9278 | 0.66667 | 305.3722 | 0.84923 | 2 | 57226.508 | 16829.8687 | 6564.1282 | 2244.2191 | NORMAL
285.9278 | 0.66667 | 305.3722 | 0.84923 | 2 | 73773.932 | 17056.6183 | 7090.5176 | 2244.2191 | NORMAL
285.9278 | 0.66667 | 305.3722 | 0.84923 | 2 | 90321.356 | 17266.1633 | 7624.0492 | 2244.2191 | NORMAL
285.9278 | 0.66667 | 305.3722 | 0.84923 | 2 | 106868.78 | 17460.5349 | 8149.9649 | 2244.2191 | NORMAL
285.9278 | 1 | 291.4833 | 0.34644 | 1 | 57226.508 | 9250.7227 | 2259.2391 | 1510.3093 | NORMAL
285.9278 | 1 | 291.4833 | 0.34644 | 1 | 73773.932 | 9250.7227 | 2831.0757 | 1510.3093 | NORMAL
285.9278 | 1 | 291.4833 | 0.34644 | 1 | 90321.356 | 9250.7227 | 3347.3221 | 1510.3093 | NORMAL
285.9278 | 1 | 291.4833 | 0.34644 | 1 | 106868.78 | 9250.7227 | 3809.0981 | 1510.3093 | NORMAL
285.9278 | 1 | 291.4833 | 0.34644 | 2 | 57226.508 | 12550.1538 | 3209.3331 | 2034.6367 | NORMAL
285.9278 | 1 | 291.4833 | 0.34644 | 2 | 73773.932 | 12550.1538 | 4055.136 | 2034.6367 | NORMAL
285.9278 | 1 | 291.4833 | 0.34644 | 2 | 90321.356 | 12550.1538 | 4819.7106 | 2034.6367 | NORMAL
285.9278 | 1 | 291.4833 | 0.34644 | 2 | 106868.78 | 12550.1538 | 5499.4455 | 2034.6367 | NORMAL
285.9278 | 1 | 291.4833 | 0.51403 | 1 | 57226.508 | 8871.6651 | 2078.378 | 1555.9 | NORMAL
285.9278 | 1 | 291.4833 | 0.51403 | 1 | 73773.932 | 8871.6651 | 2585.1087 | 1555.9 | NORMAL
285.9278 | 1 | 291.4833 | 0.51403 | 1 | 90321.356 | 8871.6651 | 3041.0604 | 1555.9 | NORMAL
285.9278 | 1 | 291.4833 | 0.51403 | 1 | 106868.78 | 8871.6651 | 3449.8278 | 1555.9 | NORMAL
285.9278 | 1 | 291.4833 | 0.51403 | 2 | 57226.508 | 12792.3435 | 3095.7671 | 2310.9113 | NORMAL
285.9278 | 1 | 291.4833 | 0.51403 | 2 | 73773.932 | 12792.3435 | 3872.9634 | 2310.9113 | NORMAL
285.9278 | 1 | 291.4833 | 0.51403 | 2 | 90321.356 | 12792.3435 | 4574.1963 | 2310.9113 | NORMAL
285.9278 | 1 | 291.4833 | 0.51403 | 2 | 106868.78 | 12792.3435 | 5201.8995 | 2310.9113 | NORMAL
285.9278 | 1 | 291.4833 | 0.68163 | 1 | 57226.508 | 8476.2871 | 1947.0024 | 1537.7545 | NORMAL
285.9278 | 1 | 291.4833 | 0.68163 | 1 | 73773.932 | 8476.2871 | 2413.2865 | 1537.7545 | NORMAL
285.9278 | 1 | 291.4833 | 0.68163 | 1 | 90321.356 | 8476.2871 | 2831.9749 | 1537.7545 | NORMAL
285.9278 | 1 | 291.4833 | 0.68163 | 1 | 106868.78 | 8476.2871 | 3207.4235 | 1537.7545 | NORMAL
285.9278 | 1 | 291.4833 | 0.68163 | 2 | 57226.508 | 12384.8662 | 2909.9613 | 2350.9439 | NORMAL
285.9278 | 1 | 291.4833 | 0.68163 | 2 | 73773.932 | 12384.8662 | 3621.3319 | 2350.9439 | NORMAL
285.9278 | 1 | 291.4833 | 0.68163 | 2 | 90321.356 | 12384.8662 | 4261.5997 | 2350.9439 | NORMAL
285.9278 | 1 | 291.4833 | 0.68163 | 2 | 106868.78 | 12384.8662 | 4835.5652 | 2350.9439 | NORMAL
285.9278 | 1 | 291.4833 | 0.84923 | 1 | 57226.508 | 8170.5874 | 1856.0616 | 1511.8517 | NORMAL
285.9278 | 1 | 291.4833 | 0.84923 | 1 | 73773.932 | 8170.5874 | 2296.1002 | 1511.8517 | NORMAL
285.9278 | 1 | 291.4833 | 0.84923 | 1 | 90321.356 | 8170.5874 | 2690.7181 | 1511.8517 | NORMAL
285.9278 | 1 | 291.4833 | 0.84923 | 1 | 106868.78 | 8170.5874 | 3044.5606 | 1511.8517 | NORMAL
285.9278 | 1 | 291.4833 | 0.84923 | 2 | 57226.508 | 11964.4937 | 2764.0776 | 2336.657 | NORMAL
285.9278 | 1 | 291.4833 | 0.84923 | 2 | 73773.932 | 11964.4937 | 3429.5067 | 2336.657 | NORMAL
285.9278 | 1 | 291.4833 | 0.84923 | 2 | 90321.356 | 11964.4937 | 4027.3901 | 2336.657 | NORMAL
285.9278 | 1 | 291.4833 | 0.84923 | 2 | 106868.78 | 11964.4937 | 4563.5163 | 2336.657 | NORMAL
285.9278 | 1 | 296.113 | 0.34644 | 1 | 57226.508 | 11046.9074 | 2166.9919 | 1450.5616 | NORMAL
285.9278 | 1 | 296.113 | 0.34644 | 1 | 73773.932 | 11046.9074 | 2766.6516 | 1450.5616 | NORMAL
285.9278 | 1 | 296.113 | 0.34644 | 1 | 90321.356 | 11046.9074 | 3328.8872 | 1450.5616 | NORMAL
285.9278 | 1 | 296.113 | 0.34644 | 1 | 106868.78 | 11046.9074 | 3850.1041 | 1450.5616 | NORMAL
285.9278 | 1 | 296.113 | 0.34644 | 2 | 57226.508 | 14986.979 | 3074.6495 | 1954.1467 | NORMAL
285.9278 | 1 | 296.113 | 0.34644 | 2 | 73773.932 | 14986.979 | 3967.9219 | 1954.1467 | NORMAL
285.9278 | 1 | 296.113 | 0.34644 | 2 | 90321.356 | 14986.979 | 4813.3275 | 1954.1467 | NORMAL
285.9278 | 1 | 296.113 | 0.34644 | 2 | 106868.78 | 14986.979 | 5598.0114 | 1954.1467 | NORMAL
285.9278 | 1 | 296.113 | 0.51403 | 1 | 57226.508 | 10594.2494 | 1996.1206 | 1494.3487 | NORMAL
285.9278 | 1 | 296.113 | 0.51403 | 1 | 73773.932 | 10594.2494 | 2524.9658 | 1494.3487 | NORMAL
285.9278 | 1 | 296.113 | 0.51403 | 1 | 90321.356 | 10594.2494 | 3016.1601 | 1494.3487 | NORMAL
285.9278 | 1 | 296.113 | 0.51403 | 1 | 106868.78 | 10594.2494 | 3469.8467 | 1494.3487 | NORMAL
285.9278 | 1 | 296.113 | 0.51403 | 2 | 57226.508 | 15276.194 | 2970.1632 | 2219.4919 | NORMAL
285.9278 | 1 | 296.113 | 0.51403 | 2 | 73773.932 | 15276.194 | 3784.2177 | 2219.4919 | NORMAL
285.9278 | 1 | 296.113 | 0.51403 | 2 | 90321.356 | 15276.194 | 4545.9298 | 2219.4919 | NORMAL
285.9278 | 1 | 296.113 | 0.51403 | 2 | 106868.78 | 15276.194 | 5251.6172 | 2219.4919 | NORMAL
285.9278 | 1 | 296.113 | 0.68163 | 1 | 57226.508 | 10122.102 | 1871.2259 | 1476.9211 | NORMAL
285.9278 | 1 | 296.113 | 0.68163 | 1 | 73773.932 | 10122.102 | 2356.9788 | 1476.9211 | NORMAL
285.9278 | 1 | 296.113 | 0.68163 | 1 | 90321.356 | 10122.102 | 2806.0841 | 1476.9211 | NORMAL
285.9278 | 1 | 296.113 | 0.68163 | 1 | 106868.78 | 10122.102 | 3219.9505 | 1476.9211 | NORMAL
285.9278 | 1 | 296.113 | 0.68163 | 2 | 57226.508 | 14789.5981 | 2794.5159 | 2257.9409 | NORMAL
285.9278 | 1 | 296.113 | 0.68163 | 2 | 73773.932 | 14789.5981 | 3537.15 | 2257.9409 | NORMAL
285.9278 | 1 | 296.113 | 0.68163 | 2 | 90321.356 | 14789.5981 | 4227.382 | 2257.9409 | NORMAL
285.9278 | 1 | 296.113 | 0.68163 | 2 | 106868.78 | 14789.5981 | 4865.1091 | 2257.9409 | NORMAL
285.9278 | 1 | 296.113 | 0.84923 | 1 | 57226.508 | 9757.0455 | 1784.5433 | 1452.043 | NORMAL
285.9278 | 1 | 296.113 | 0.84923 | 1 | 73773.932 | 9757.0455 | 2242.5407 | 1452.043 | NORMAL
285.9278 | 1 | 296.113 | 0.84923 | 1 | 90321.356 | 9757.0455 | 2664.8879 | 1452.043 | NORMAL
285.9278 | 1 | 296.113 | 0.84923 | 1 | 106868.78 | 9757.0455 | 3053.5551 | 1452.043 | NORMAL
285.9278 | 1 | 296.113 | 0.84923 | 2 | 57226.508 | 14287.6032 | 2655.9597 | 2244.2191 | NORMAL
285.9278 | 1 | 296.113 | 0.84923 | 2 | 73773.932 | 14287.6032 | 3349.5192 | 2244.2191 | NORMAL
285.9278 | 1 | 296.113 | 0.84923 | 2 | 90321.356 | 14287.6032 | 3991.6133 | 2244.2191 | NORMAL
285.9278 | 1 | 296.113 | 0.84923 | 2 | 106868.78 | 14287.6032 | 4583.7351 | 2244.2191 | NORMAL
285.9278 | 1 | 300.7426 | 0.34644 | 1 | 57226.508 | 13915.3744 | 2194.5609 | 1450.5616 | NORMAL
285.9278 | 1 | 300.7426 | 0.34644 | 1 | 73773.932 | 13915.3744 | 2854.1186 | 1450.5616 | NORMAL
285.9278 | 1 | 300.7426 | 0.34644 | 1 | 90321.356 | 13915.3744 | 3494.4992 | 1450.5616 | NORMAL
285.9278 | 1 | 300.7426 | 0.34644 | 1 | 106868.78 | 13915.3744 | 4108.7456 | 1450.5616 | NORMAL
285.9278 | 1 | 300.7426 | 0.34644 | 2 | 57226.508 | 18878.5347 | 3116.2274 | 1954.1467 | NORMAL
285.9278 | 1 | 300.7426 | 0.34644 | 2 | 73773.932 | 18878.5347 | 4108.6086 | 1954.1467 | NORMAL
285.9278 | 1 | 300.7426 | 0.34644 | 2 | 90321.356 | 18878.5347 | 5089.6598 | 1954.1467 | NORMAL
285.9278 | 1 | 300.7426 | 0.34644 | 2 | 106868.78 | 18878.5347 | 6039.7585 | 1954.1467 | NORMAL
285.9278 | 1 | 300.7426 | 0.51403 | 1 | 57226.508 | 13345.1782 | 2020.7648 | 1494.3487 | NORMAL
285.9278 | 1 | 300.7426 | 0.51403 | 1 | 73773.932 | 13345.1782 | 2598.2162 | 1494.3487 | NORMAL
285.9278 | 1 | 300.7426 | 0.51403 | 1 | 90321.356 | 13345.1782 | 3150.0806 | 1494.3487 | NORMAL
285.9278 | 1 | 300.7426 | 0.51403 | 1 | 106868.78 | 13345.1782 | 3674.0325 | 1494.3487 | NORMAL
285.9278 | 1 | 300.7426 | 0.51403 | 2 | 57226.508 | 19242.848 | 3007.6254 | 2219.4919 | NORMAL
285.9278 | 1 | 300.7426 | 0.51403 | 2 | 73773.932 | 19242.848 | 3901.4426 | 2219.4919 | NORMAL
285.9278 | 1 | 300.7426 | 0.51403 | 2 | 90321.356 | 19242.848 | 4766.2093 | 2219.4919 | NORMAL
285.9278 | 1 | 300.7426 | 0.51403 | 2 | 106868.78 | 19242.848 | 5593.8804 | 2219.4919 | NORMAL
285.9278 | 1 | 300.7426 | 0.68163 | 1 | 57226.508 | 12750.4318 | 1894.1889 | 1476.9211 | NORMAL
285.9278 | 1 | 300.7426 | 0.68163 | 1 | 73773.932 | 12750.4318 | 2423.0328 | 1476.9211 | NORMAL
285.9278 | 1 | 300.7426 | 0.68163 | 1 | 90321.356 | 12750.4318 | 2924.823 | 1476.9211 | NORMAL
285.9278 | 1 | 300.7426 | 0.68163 | 1 | 106868.78 | 12750.4318 | 3398.8631 | 1476.9211 | NORMAL
285.9278 | 1 | 300.7426 | 0.68163 | 2 | 57226.508 | 18629.9013 | 2829.0635 | 2257.9409 | NORMAL
285.9278 | 1 | 300.7426 | 0.68163 | 2 | 73773.932 | 18629.9013 | 3640.3301 | 2257.9409 | NORMAL
285.9278 | 1 | 300.7426 | 0.68163 | 2 | 90321.356 | 18629.9013 | 4416.4956 | 2257.9409 | NORMAL
285.9278 | 1 | 300.7426 | 0.68163 | 2 | 106868.78 | 18629.9013 | 5153.9505 | 2257.9409 | NORMAL
285.9278 | 1 | 300.7426 | 0.84923 | 1 | 57226.508 | 12290.5838 | 1806.4168 | 1452.043 | NORMAL
285.9278 | 1 | 300.7426 | 0.84923 | 1 | 73773.932 | 12290.5838 | 2304.2849 | 1452.043 | NORMAL
285.9278 | 1 | 300.7426 | 0.84923 | 1 | 90321.356 | 12290.5838 | 2774.8223 | 1452.043 | NORMAL
285.9278 | 1 | 300.7426 | 0.84923 | 1 | 106868.78 | 12290.5838 | 3218.0941 | 1452.043 | NORMAL
285.9278 | 1 | 300.7426 | 0.84923 | 2 | 57226.508 | 17997.5572 | 2688.5929 | 2244.2191 | NORMAL
285.9278 | 1 | 300.7426 | 0.84923 | 2 | 73773.932 | 17997.5572 | 3444.3003 | 2244.2191 | NORMAL
285.9278 | 1 | 300.7426 | 0.84923 | 2 | 90321.356 | 17997.5572 | 4162.8363 | 2244.2191 | NORMAL
285.9278 | 1 | 300.7426 | 0.84923 | 2 | 106868.78 | 17997.5572 | 4842.6235 | 2244.2191 | NORMAL
285.9278 | 1 | 305.3722 | 0.34644 | 1 | 57226.508 | 17856.1237 | 2256.3659 | 1450.5616 | NORMAL
285.9278 | 1 | 305.3722 | 0.34644 | 1 | 73773.932 | 17856.1237 | 2988.0842 | 1450.5616 | NORMAL
285.9278 | 1 | 305.3722 | 0.34644 | 1 | 90321.356 | 17856.1237 | 3722.077 | 1450.5616 | NORMAL
285.9278 | 1 | 305.3722 | 0.34644 | 1 | 106868.78 | 17856.1237 | 4450.09 | 1450.5616 | NORMAL
285.9278 | 1 | 305.3722 | 0.34644 | 2 | 57226.508 | 24224.8207 | 3206.9496 | 1954.1467 | NORMAL
285.9278 | 1 | 305.3722 | 0.34644 | 2 | 73773.932 | 24224.8207 | 4319.2076 | 1954.1467 | NORMAL
285.9278 | 1 | 305.3722 | 0.34644 | 2 | 90321.356 | 24224.8207 | 5466.5774 | 1954.1467 | NORMAL
285.9278 | 1 | 305.3722 | 0.34644 | 2 | 106868.78 | 24224.8207 | 6628.1094 | 1954.1467 | NORMAL
285.9278 | 1 | 305.3722 | 0.51403 | 1 | 57226.508 | 17124.4513 | 2076.7221 | 1494.3487 | NORMAL
285.9278 | 1 | 305.3722 | 0.51403 | 1 | 73773.932 | 17124.4513 | 2712.7251 | 1494.3487 | NORMAL
285.9278 | 1 | 305.3722 | 0.51403 | 1 | 90321.356 | 17124.4513 | 3336.3381 | 1494.3487 | NORMAL
285.9278 | 1 | 305.3722 | 0.51403 | 1 | 106868.78 | 17124.4513 | 3943.8297 | 1494.3487 | NORMAL
285.9278 | 1 | 305.3722 | 0.51403 | 2 | 57226.508 | 24692.3053 | 3091.9276 | 2219.4919 | NORMAL
285.9278 | 1 | 305.3722 | 0.51403 | 2 | 73773.932 | 24692.3053 | 4081.8108 | 2219.4919 | NORMAL
285.9278 | 1 | 305.3722 | 0.51403 | 2 | 90321.356 | 24692.3053 | 5069.6058 | 2219.4919 | NORMAL
285.9278 | 1 | 305.3722 | 0.51403 | 2 | 106868.78 | 24692.3053 | 6045.3921 | 2219.4919 | NORMAL
285.9278 | 1 | 305.3722 | 0.68163 | 1 | 57226.508 | 16361.2764 | 1946.4365 | 1476.9211 | NORMAL
285.9278 | 1 | 305.3722 | 0.68163 | 1 | 73773.932 | 16361.2764 | 2527.2329 | 1476.9211 | NORMAL
285.9278 | 1 | 305.3722 | 0.68163 | 1 | 90321.356 | 16361.2764 | 3091.0901 | 1476.9211 | NORMAL
285.9278 | 1 | 305.3722 | 0.68163 | 1 | 106868.78 | 16361.2764 | 3635.9785 | 1476.9211 | NORMAL
285.9278 | 1 | 305.3722 | 0.68163 | 2 | 57226.508 | 23905.7759 | 2907.4665 | 2257.9409 | NORMAL
285.9278 | 1 | 305.3722 | 0.68163 | 2 | 73773.932 | 23905.7759 | 3801.4017 | 2257.9409 | NORMAL
285.9278 | 1 | 305.3722 | 0.68163 | 2 | 90321.356 | 23905.7759 | 4679.2621 | 2257.9409 | NORMAL
285.9278 | 1 | 305.3722 | 0.68163 | 2 | 106868.78 | 23905.7759 | 5535.4802 | 2257.9409 | NORMAL
285.9278 | 1 | 305.3722 | 0.84923 | 1 | 57226.508 | 15771.2023 | 1856.1887 | 1452.043 | NORMAL
285.9278 | 1 | 305.3722 | 0.84923 | 1 | 73773.932 | 15771.2023 | 2402.1601 | 1452.043 | NORMAL
285.9278 | 1 | 305.3722 | 0.84923 | 1 | 90321.356 | 15771.2023 | 2929.3789 | 1452.043 | NORMAL
285.9278 | 1 | 305.3722 | 0.84923 | 1 | 106868.78 | 15771.2023 | 3436.6494 | 1452.043 | NORMAL
285.9278 | 1 | 305.3722 | 0.84923 | 2 | 57226.508 | 23094.3557 | 2762.8178 | 2244.2191 | NORMAL
285.9278 | 1 | 305.3722 | 0.84923 | 2 | 73773.932 | 23094.3557 | 3593.4309 | 2244.2191 | NORMAL
285.9278 | 1 | 305.3722 | 0.84923 | 2 | 90321.356 | 23094.3557 | 4402.11 | 2244.2191 | NORMAL
285.9278 | 1 | 305.3722 | 0.84923 | 2 | 106868.78 | 23094.3557 | 5185.3845 | 2244.2191 | NORMAL
298.8907 | 0 | 291.4833 | 0.34644 | 1 | 57226.508 | 12163.6844 | 12831.8541 | 1504.0021 | NORMAL
298.8907 | 0 | 291.4833 | 0.34644 | 1 | 73773.932 | 10985.4515 | 11718.338 | 1504.0021 | NORMAL
298.8907 | 0 | 291.4833 | 0.34644 | 1 | 90321.356 | 10215.4304 | 10967.3894 | 1504.0021 | NORMAL
298.8907 | 0 | 291.4833 | 0.34644 | 1 | 106868.78 | 9680.5263 | 10427.0831 | 1504.0021 | NORMAL
298.8907 | 0 | 291.4833 | 0.34644 | 2 | 57226.508 | 16502.0739 | 16785.2684 | 2026.1399 | NORMAL
298.8907 | 0 | 291.4833 | 0.34644 | 2 | 73773.932 | 14903.6038 | 15257.0682 | 2026.1399 | NORMAL
298.8907 | 0 | 291.4833 | 0.34644 | 2 | 90321.356 | 13858.9413 | 14250.2371 | 2026.1399 | NORMAL
298.8907 | 0 | 291.4833 | 0.34644 | 2 | 106868.78 | 13133.2543 | 13540.9112 | 2026.1399 | NORMAL
298.8907 | 0 | 291.4833 | 0.51403 | 1 | 57226.508 | 11665.2654 | 13479.458 | 1549.4024 | NORMAL
298.8907 | 0 | 291.4833 | 0.51403 | 1 | 73773.932 | 10535.3117 | 12351.6806 | 1549.4024 | NORMAL
298.8907 | 0 | 291.4833 | 0.51403 | 1 | 90321.356 | 9796.843 | 11563.8522 | 1549.4024 | NORMAL
298.8907 | 0 | 291.4833 | 0.51403 | 1 | 106868.78 | 9283.8571 | 10980.3383 | 1549.4024 | NORMAL
298.8907 | 0 | 291.4833 | 0.51403 | 2 | 57226.508 | 16820.5269 | 17981.977 | 2301.2608 | NORMAL
298.8907 | 0 | 291.4833 | 0.51403 | 2 | 73773.932 | 15191.2098 | 16436.8734 | 2301.2608 | NORMAL
298.8907 | 0 | 291.4833 | 0.51403 | 2 | 90321.356 | 14126.3877 | 15387.8281 | 2301.2608 | NORMAL
298.8907 | 0 | 291.4833 | 0.51403 | 2 | 106868.78 | 13386.6966 | 14628.7632 | 2301.2608 | NORMAL
298.8907 | 0 | 291.4833 | 0.68163 | 1 | 57226.508 | 11145.3867 | 14012.3284 | 1531.3327 | NORMAL
298.8907 | 0 | 291.4833 | 0.68163 | 1 | 73773.932 | 10065.791 | 12843.2976 | 1531.3327 | NORMAL
298.8907 | 0 | 291.4833 | 0.68163 | 1 | 90321.356 | 9360.2331 | 12010.727 | 1531.3327 | NORMAL
298.8907 | 0 | 291.4833 | 0.68163 | 1 | 106868.78 | 8870.1092 | 11384.2754 | 1531.3327 | NORMAL
298.8907 | 0 | 291.4833 | 0.68163 | 2 | 57226.508 | 16284.739 | 18636.9246 | 2341.1262 | NORMAL
298.8907 | 0 | 291.4833 | 0.68163 | 2 | 73773.932 | 14707.3209 | 17075.2822 | 2341.1262 | NORMAL
298.8907 | 0 | 291.4833 | 0.68163 | 2 | 90321.356 | 13676.4168 | 15987.4223 | 2341.1262 | NORMAL
298.8907 | 0 | 291.4833 | 0.68163 | 2 | 106868.78 | 12960.2872 | 15183.5214 | 2341.1262 | NORMAL
298.8907 | 0 | 291.4833 | 0.84923 | 1 | 57226.508 | 10743.4251 | 14452.4274 | 1505.538 | NORMAL
298.8907 | 0 | 291.4833 | 0.84923 | 1 | 73773.932 | 9702.7653 | 13240.3528 | 1505.538 | NORMAL
298.8907 | 0 | 291.4833 | 0.84923 | 1 | 90321.356 | 9022.6537 | 12367.6146 | 1505.538 | NORMAL
298.8907 | 0 | 291.4833 | 0.84923 | 1 | 106868.78 | 8550.2061 | 11704.9684 | 1505.538 | NORMAL
298.8907 | 0 | 291.4833 | 0.84923 | 2 | 57226.508 | 15731.9953 | 19220.0976 | 2326.8989 | NORMAL
298.8907 | 0 | 291.4833 | 0.84923 | 2 | 73773.932 | 14208.1187 | 17617.6037 | 2326.8989 | NORMAL
298.8907 | 0 | 291.4833 | 0.84923 | 2 | 90321.356 | 13212.2059 | 16482.796 | 2326.8989 | NORMAL
298.8907 | 0 | 291.4833 | 0.84923 | 2 | 106868.78 | 12520.3836 | 15632.9012 | 2326.8989 | NORMAL
298.8907 | 0 | 296.113 | 0.34644 | 1 | 57226.508 | 10975.2412 | 12236.4046 | 1504.0021 | NORMAL
298.8907 | 0 | 296.113 | 0.34644 | 1 | 73773.932 | 9921.3865 | 11236.1568 | 1504.0021 | NORMAL
298.8907 | 0 | 296.113 | 0.34644 | 1 | 90321.356 | 9261.5471 | 10565.0821 | 1504.0021 | NORMAL
298.8907 | 0 | 296.113 | 0.34644 | 1 | 106868.78 | 8825.8116 | 10087.4269 | 1504.0021 | NORMAL
298.8907 | 0 | 296.113 | 0.34644 | 2 | 57226.508 | 14889.7519 | 15557.0139 | 2026.1399 | NORMAL
298.8907 | 0 | 296.113 | 0.34644 | 2 | 73773.932 | 13460.0215 | 14223.8562 | 2026.1399 | NORMAL
298.8907 | 0 | 296.113 | 0.34644 | 2 | 90321.356 | 12564.839 | 13361.7593 | 2026.1399 | NORMAL
298.8907 | 0 | 296.113 | 0.34644 | 2 | 106868.78 | 11973.6907 | 12768.1466 | 2026.1399 | NORMAL
298.8907 | 0 | 296.113 | 0.51403 | 1 | 57226.508 | 10525.5199 | 13378.2007 | 1549.4024 | NORMAL
298.8907 | 0 | 296.113 | 0.51403 | 1 | 73773.932 | 9514.8479 | 12307.3818 | 1549.4024 | NORMAL
298.8907 | 0 | 296.113 | 0.51403 | 1 | 90321.356 | 8882.0461 | 11557.8904 | 1549.4024 | NORMAL
298.8907 | 0 | 296.113 | 0.51403 | 1 | 106868.78 | 8464.1652 | 11004.2934 | 1549.4024 | NORMAL
298.8907 | 0 | 296.113 | 0.51403 | 2 | 57226.508 | 15177.0906 | 17278.4722 | 2301.2608 | NORMAL
298.8907 | 0 | 296.113 | 0.51403 | 2 | 73773.932 | 13719.7697 | 15876.4356 | 2301.2608 | NORMAL
298.8907 | 0 | 296.113 | 0.51403 | 2 | 90321.356 | 12807.3121 | 14927.4675 | 2301.2608 | NORMAL
298.8907 | 0 | 296.113 | 0.51403 | 2 | 106868.78 | 12204.756 | 14246.7725 | 2301.2608 | NORMAL
298.8907 | 0 | 296.113 | 0.68163 | 1 | 57226.508 | 10056.4355 | 14238.1308 | 1531.3327 | NORMAL
298.8907 | 0 | 296.113 | 0.68163 | 1 | 73773.932 | 9090.8055 | 13093.0064 | 1531.3327 | NORMAL
298.8907 | 0 | 296.113 | 0.68163 | 1 | 90321.356 | 8486.2054 | 12274.6379 | 1531.3327 | NORMAL
298.8907 | 0 | 296.113 | 0.68163 | 1 | 106868.78 | 8086.948 | 11658.9737 | 1531.3327 | NORMAL
298.8907 | 0 | 296.113 | 0.68163 | 2 | 57226.508 | 14693.6514 | 18436.6291 | 2341.1262 | NORMAL
298.8907 | 0 | 296.113 | 0.68163 | 2 | 73773.932 | 13282.7509 | 16960.5777 | 2341.1262 | NORMAL
298.8907 | 0 | 296.113 | 0.68163 | 2 | 90321.356 | 12399.358 | 15930.6652 | 2341.1262 | NORMAL
298.8907 | 0 | 296.113 | 0.68163 | 2 | 106868.78 | 11815.9953 | 15172.0121 | 2341.1262 | NORMAL
298.8907 | 0 | 296.113 | 0.84923 | 1 | 57226.508 | 9693.7473 | 14899.3887 | 1505.538 | NORMAL
298.8907 | 0 | 296.113 | 0.84923 | 1 | 73773.932 | 8762.943 | 13691.4168 | 1505.538 | NORMAL
298.8907 | 0 | 296.113 | 0.84923 | 1 | 90321.356 | 8180.148 | 12818.1409 | 1505.538 | NORMAL
298.8907 | 0 | 296.113 | 0.84923 | 1 | 106868.78 | 7795.2899 | 12154.4117 | 1505.538 | NORMAL
298.8907 | 0 | 296.113 | 0.84923 | 2 | 57226.508 | 14194.9132 | 19390.7245 | 2326.8989 | NORMAL
298.8907 | 0 | 296.113 | 0.84923 | 2 | 73773.932 | 12831.902 | 17835.2427 | 2326.8989 | NORMAL
298.8907 | 0 | 296.113 | 0.84923 | 2 | 90321.356 | 11978.4937 | 16730.3057 | 2326.8989 | NORMAL
298.8907 | 0 | 296.113 | 0.84923 | 2 | 106868.78 | 11414.9317 | 15903.4826 | 2326.8989 | NORMAL
298.8907 | 0 | 300.7426 | 0.34644 | 1 | 57226.508 | 10043.327 | 12080.99 | 1504.0021 | NORMAL
298.8907 | 0 | 300.7426 | 0.34644 | 1 | 73773.932 | 9132.2663 | 11175.1551 | 1504.0021 | NORMAL
298.8907 | 0 | 300.7426 | 0.34644 | 1 | 90321.356 | 8599.52 | 10571.6894 | 1504.0021 | NORMAL
298.8907 | 0 | 300.7426 | 0.34644 | 1 | 106868.78 | 8278.7985 | 10149.0748 | 1504.0021 | NORMAL
298.8907 | 0 | 300.7426 | 0.34644 | 2 | 57226.508 | 13625.4543 | 14898.0273 | 2026.1399 | NORMAL
298.8907 | 0 | 300.7426 | 0.34644 | 2 | 73773.932 | 12389.4479 | 13747.2587 | 2026.1399 | NORMAL
298.8907 | 0 | 300.7426 | 0.34644 | 2 | 90321.356 | 11666.6884 | 13017.4647 | 2026.1399 | NORMAL
298.8907 | 0 | 300.7426 | 0.34644 | 2 | 106868.78 | 11231.576 | 12530.6975 | 2026.1399 | NORMAL
298.8907 | 0 | 300.7426 | 0.51403 | 1 | 57226.508 | 9631.7918 | 13683.4747 | 1549.4024 | NORMAL
298.8907 | 0 | 300.7426 | 0.51403 | 1 | 73773.932 | 8758.0627 | 12656.7627 | 1549.4024 | NORMAL
298.8907 | 0 | 300.7426 | 0.51403 | 1 | 90321.356 | 8247.1462 | 11938.7048 | 1549.4024 | NORMAL
298.8907 | 0 | 300.7426 | 0.51403 | 1 | 106868.78 | 7939.5666 | 11411.593 | 1549.4024 | NORMAL
298.8907 | 0 | 300.7426 | 0.51403 | 2 | 57226.508 | 13888.3949 | 17182.0368 | 2301.2608 | NORMAL
298.8907 | 0 | 300.7426 | 0.51403 | 2 | 73773.932 | 12628.5364 | 15897.047 | 2301.2608 | NORMAL
298.8907 | 0 | 300.7426 | 0.51403 | 2 | 90321.356 | 11891.8292 | 15031.8853 | 2301.2608 | NORMAL
298.8907 | 0 | 300.7426 | 0.51403 | 2 | 106868.78 | 11448.3202 | 14419.7255 | 2301.2608 | NORMAL
298.8907 | 0 | 300.7426 | 0.68163 | 1 | 57226.508 | 9202.5376 | 14840.686 | 1531.3327 | NORMAL
298.8907 | 0 | 300.7426 | 0.68163 | 1 | 73773.932 | 8367.7475 | 13712.8668 | 1531.3327 | NORMAL
298.8907 | 0 | 300.7426 | 0.68163 | 1 | 90321.356 | 7879.6007 | 12904.6139 | 1531.3327 | NORMAL
298.8907 | 0 | 300.7426 | 0.68163 | 1 | 106868.78 | 7585.7288 | 12265.2038 | 1531.3327 | NORMAL
298.8907 | 0 | 300.7426 | 0.68163 | 2 | 57226.508 | 13446.0049 | 18806.3604 | 2341.1262 | NORMAL
298.8907 | 0 | 300.7426 | 0.68163 | 2 | 73773.932 | 12226.2769 | 17396.9184 | 2341.1262 | NORMAL
298.8907 | 0 | 300.7426 | 0.68163 | 2 | 90321.356 | 11513.0362 | 16414.5574 | 2341.1262 | NORMAL
298.8907 | 0 | 300.7426 | 0.68163 | 2 | 106868.78 | 11083.6543 | 15695.8015 | 2341.1262 | NORMAL
298.8907 | 0 | 300.7426 | 0.84923 | 1 | 57226.508 | 8870.6455 | 15704.6226 | 1505.538 | NORMAL
298.8907 | 0 | 300.7426 | 0.84923 | 1 | 73773.932 | 8065.9623 | 14497.9394 | 1505.538 | NORMAL
298.8907 | 0 | 300.7426 | 0.84923 | 1 | 90321.356 | 7595.4206 | 13587.9349 | 1505.538 | NORMAL
298.8907 | 0 | 300.7426 | 0.84923 | 1 | 106868.78 | 7312.1473 | 12886.3851 | 1505.538 | NORMAL
298.8907 | 0 | 300.7426 | 0.84923 | 2 | 57226.508 | 12989.6148 | 20097.7465 | 2326.8989 | NORMAL
298.8907 | 0 | 300.7426 | 0.84923 | 2 | 73773.932 | 11811.2873 | 18577.4314 | 2326.8989 | NORMAL
298.8907 | 0 | 300.7426 | 0.84923 | 2 | 90321.356 | 11122.2558 | 17496.9331 | 2326.8989 | NORMAL
298.8907 | 0 | 300.7426 | 0.84923 | 2 | 106868.78 | 10707.4482 | 16664.7188 | 2326.8989 | NORMAL
298.8907 | 0 | 305.3722 | 0.34644 | 1 | 57226.508 | 9324.5978 | 12267.5211 | 1504.0021 | NORMAL
298.8907 | 0 | 305.3722 | 0.34644 | 1 | 73773.932 | 8571.1607 | 11436.4271 | 1504.0021 | NORMAL
298.8907 | 0 | 305.3722 | 0.34644 | 1 | 90321.356 | 8178.9682 | 10888.3646 | 1504.0021 | NORMAL
298.8907 | 0 | 305.3722 | 0.34644 | 1 | 106868.78 | 7985.6412 | 10512.8692 | 1504.0021 | NORMAL
298.8907 | 0 | 305.3722 | 0.34644 | 2 | 57226.508 | 12650.3778 | 14718.8389 | 2026.1399 | NORMAL
298.8907 | 0 | 305.3722 | 0.34644 | 2 | 73773.932 | 11628.2142 | 13720.3574 | 2026.1399 | NORMAL
298.8907 | 0 | 305.3722 | 0.34644 | 2 | 90321.356 | 11096.1394 | 13102.0149 | 2026.1399 | NORMAL
298.8907 | 0 | 305.3722 | 0.34644 | 2 | 106868.78 | 10833.8589 | 12707.9559 | 2026.1399 | NORMAL
298.8907 | 0 | 305.3722 | 0.51403 | 1 | 57226.508 | 8942.5132 | 14294.1172 | 1549.4024 | NORMAL
298.8907 | 0 | 305.3722 | 0.51403 | 1 | 73773.932 | 8219.9489 | 13301.6833 | 1549.4024 | NORMAL
298.8907 | 0 | 305.3722 | 0.51403 | 1 | 90321.356 | 7843.8269 | 12580.9347 | 1549.4024 | NORMAL
298.8907 | 0 | 305.3722 | 0.51403 | 1 | 106868.78 | 7658.4216 | 12048.1891 | 1549.4024 | NORMAL
298.8907 | 0 | 305.3722 | 0.51403 | 2 | 57226.508 | 12894.5016 | 17551.8726 | 2301.2608 | NORMAL
298.8907 | 0 | 305.3722 | 0.51403 | 2 | 73773.932 | 11852.6126 | 16359.02 | 2301.2608 | NORMAL
298.8907 | 0 | 305.3722 | 0.51403 | 2 | 90321.356 | 11310.27 | 15562.4568 | 2301.2608 | NORMAL
298.8907 | 0 | 305.3722 | 0.51403 | 2 | 106868.78 | 11042.9281 | 15009.0598 | 2301.2608 | NORMAL
298.8907 | 0 | 305.3722 | 0.68163 | 1 | 57226.508 | 8543.9777 | 15726.8907 | 1531.3327 | NORMAL
298.8907 | 0 | 305.3722 | 0.68163 | 1 | 73773.932 | 7853.6155 | 14575.1657 | 1531.3327 | NORMAL
298.8907 | 0 | 305.3722 | 0.68163 | 1 | 90321.356 | 7494.2559 | 13726.1464 | 1531.3327 | NORMAL
298.8907 | 0 | 305.3722 | 0.68163 | 1 | 106868.78 | 7317.1134 | 13095.4444 | 1531.3327 | NORMAL
298.8907 | 0 | 305.3722 | 0.68163 | 2 | 57226.508 | 12483.7703 | 19604.5669 | 2341.1262 | NORMAL
298.8907 | 0 | 305.3722 | 0.68163 | 2 | 73773.932 | 11475.0687 | 18246.9636 | 2341.1262 | NORMAL
298.8907 | 0 | 305.3722 | 0.68163 | 2 | 90321.356 | 10950.0015 | 17273.9375 | 2341.1262 | NORMAL
298.8907 | 0 | 305.3722 | 0.68163 | 2 | 106868.78 | 10691.1753 | 16551.038 | 2341.1262 | NORMAL
298.8907 | 0 | 305.3722 | 0.84923 | 1 | 57226.508 | 8235.8367 | 16781.3551 | 1505.538 | NORMAL
298.8907 | 0 | 305.3722 | 0.84923 | 1 | 73773.932 | 7570.3726 | 15497.956 | 1505.538 | NORMAL
298.8907 | 0 | 305.3722 | 0.84923 | 1 | 90321.356 | 7223.9734 | 14565.3777 | 1505.538 | NORMAL
298.8907 | 0 | 305.3722 | 0.84923 | 1 | 106868.78 | 7053.2197 | 13863.2616 | 1505.538 | NORMAL
298.8907 | 0 | 305.3722 | 0.84923 | 2 | 57226.508 | 12060.0407 | 21207.8408 | 2326.8989 | NORMAL
298.8907 | 0 | 305.3722 | 0.84923 | 2 | 73773.932 | 11085.577 | 19687.1471 | 2326.8989 | NORMAL
298.8907 | 0 | 305.3722 | 0.84923 | 2 | 90321.356 | 10578.3318 | 18558.6975 | 2326.8989 | NORMAL
298.8907 | 0 | 305.3722 | 0.84923 | 2 | 106868.78 | 10328.2908 | 17726.3904 | 2326.8989 | NORMAL
298.8907 | 0.33333 | 291.4833 | 0.34644 | 1 | 57226.508 | 8716.3861 | 6721.7509 | 1504.0021 | NORMAL
298.8907 | 0.33333 | 291.4833 | 0.34644 | 1 | 73773.932 | 8479.7206 | 6832.9826 | 1504.0021 | NORMAL
298.8907 | 0.33333 | 291.4833 | 0.34644 | 1 | 90321.356 | 8316.4267 | 6914.3681 | 1504.0021 | NORMAL
298.8907 | 0.33333 | 291.4833 | 0.34644 | 1 | 106868.78 | 8200.5843 | 6978.8193 | 1504.0021 | NORMAL
298.8907 | 0.33333 | 291.4833 | 0.34644 | 2 | 57226.508 | 11825.2368 | 8467.8064 | 2026.1399 | NORMAL
298.8907 | 0.33333 | 291.4833 | 0.34644 | 2 | 73773.932 | 11504.1604 | 8736.4412 | 2026.1399 | NORMAL
298.8907 | 0.33333 | 291.4833 | 0.34644 | 2 | 90321.356 | 11282.6249 | 8931.3181 | 2026.1399 | NORMAL
298.8907 | 0.33333 | 291.4833 | 0.34644 | 2 | 106868.78 | 11125.4653 | 9081.9649 | 2026.1399 | NORMAL
298.8907 | 0.33333 | 291.4833 | 0.51403 | 1 | 57226.508 | 8359.2236 | 7404.4613 | 1549.4024 | NORMAL
298.8907 | 0.33333 | 291.4833 | 0.51403 | 1 | 73773.932 | 8132.2557 | 7389.7589 | 1549.4024 | NORMAL
298.8907 | 0.33333 | 291.4833 | 0.51403 | 1 | 90321.356 | 7975.6529 | 7373.5424 | 1549.4024 | NORMAL
298.8907 | 0.33333 | 291.4833 | 0.51403 | 1 | 106868.78 | 7864.5573 | 7359.9917 | 1549.4024 | NORMAL
298.8907 | 0.33333 | 291.4833 | 0.51403 | 2 | 57226.508 | 12053.4373 | 9510.6517 | 2301.2608 | NORMAL
298.8907 | 0.33333 | 291.4833 | 0.51403 | 2 | 73773.932 | 11726.1649 | 9633.1849 | 2301.2608 | NORMAL
298.8907 | 0.33333 | 291.4833 | 0.51403 | 2 | 90321.356 | 11500.3542 | 9722.129 | 2301.2608 | NORMAL
298.8907 | 0.33333 | 291.4833 | 0.51403 | 2 | 106868.78 | 11340.1618 | 9792.8058 | 2301.2608 | NORMAL
298.8907 | 0.33333 | 291.4833 | 0.68163 | 1 | 57226.508 | 7986.6832 | 7840.7571 | 1531.3327 | NORMAL
298.8907 | 0.33333 | 291.4833 | 0.68163 | 1 | 73773.932 | 7769.8304 | 7739.8426 | 1531.3327 | NORMAL
298.8907 | 0.33333 | 291.4833 | 0.68163 | 1 | 90321.356 | 7620.2069 | 7656.1548 | 1531.3327 | NORMAL
298.8907 | 0.33333 | 291.4833 | 0.68163 | 1 | 106868.78 | 7514.0624 | 7587.9271 | 1531.3327 | NORMAL
298.8907 | 0.33333 | 291.4833 | 0.68163 | 2 | 57226.508 | 11669.4966 | 10205.3477 | 2341.1262 | NORMAL
298.8907 | 0.33333 | 291.4833 | 0.68163 | 2 | 73773.932 | 11352.6488 | 10199.173 | 2341.1262 | NORMAL
298.8907 | 0.33333 | 291.4833 | 0.68163 | 2 | 90321.356 | 11134.0309 | 10188.5547 | 2341.1262 | NORMAL
298.8907 | 0.33333 | 291.4833 | 0.68163 | 2 | 106868.78 | 10978.9412 | 10179.5091 | 2341.1262 | NORMAL
298.8907 | 0.33333 | 291.4833 | 0.84923 | 1 | 57226.508 | 7698.6412 | 8167.5659 | 1505.538 | NORMAL
298.8907 | 0.33333 | 291.4833 | 0.84923 | 1 | 73773.932 | 7489.6093 | 8005.6351 | 1505.538 | NORMAL
298.8907 | 0.33333 | 291.4833 | 0.84923 | 1 | 90321.356 | 7345.3819 | 7873.7027 | 1505.538 | NORMAL
298.8907 | 0.33333 | 291.4833 | 0.84923 | 1 | 106868.78 | 7243.0656 | 7766.0166 | 1505.538 | NORMAL
298.8907 | 0.33333 | 291.4833 | 0.84923 | 2 | 57226.508 | 11273.4055 | 10697.9244 | 2326.8989 | NORMAL
298.8907 | 0.33333 | 291.4833 | 0.84923 | 2 | 73773.932 | 10967.3123 | 10596.1312 | 2326.8989 | NORMAL
298.8907 | 0.33333 | 291.4833 | 0.84923 | 2 | 90321.356 | 10756.1148 | 10510.0667 | 2326.8989 | NORMAL
298.8907 | 0.33333 | 291.4833 | 0.84923 | 2 | 106868.78 | 10606.2892 | 10439.86 | 2326.8989 | NORMAL
298.8907 | 0.33333 | 296.113 | 0.34644 | 1 | 57226.508 | 8034.6418 | 6374.8285 | 1504.0021 | NORMAL
298.8907 | 0.33333 | 296.113 | 0.34644 | 1 | 73773.932 | 7951.8234 | 6502.5152 | 1504.0021 | NORMAL
298.8907 | 0.33333 | 296.113 | 0.34644 | 1 | 90321.356 | 7913.0437 | 6617.9652 | 1504.0021 | NORMAL
298.8907 | 0.33333 | 296.113 | 0.34644 | 1 | 106868.78 | 7901.6565 | 6724.5312 | 1504.0021 | NORMAL
298.8907 | 0.33333 | 296.113 | 0.34644 | 2 | 57226.508 | 10900.3365 | 7795.6284 | 2026.1399 | NORMAL
298.8907 | 0.33333 | 296.113 | 0.34644 | 2 | 73773.932 | 10787.9794 | 8076.2685 | 2026.1399 | NORMAL
298.8907 | 0.33333 | 296.113 | 0.34644 | 2 | 90321.356 | 10735.3684 | 8321.52 | 2026.1399 | NORMAL
298.8907 | 0.33333 | 296.113 | 0.34644 | 2 | 106868.78 | 10719.9197 | 8539.8969 | 2026.1399 | NORMAL
298.8907 | 0.33333 | 296.113 | 0.51403 | 1 | 57226.508 | 7705.4144 | 7223.2636 | 1549.4024 | NORMAL
298.8907 | 0.33333 | 296.113 | 0.51403 | 1 | 73773.932 | 7625.9895 | 7219.7132 | 1549.4024 | NORMAL
298.8907 | 0.33333 | 296.113 | 0.51403 | 1 | 90321.356 | 7588.7989 | 7228.5302 | 1549.4024 | NORMAL
298.8907 | 0.33333 | 296.113 | 0.51403 | 1 | 106868.78 | 7577.8783 | 7246.3312 | 1549.4024 | NORMAL
298.8907 | 0.33333 | 296.113 | 0.51403 | 2 | 57226.508 | 11110.6885 | 9073.884 | 2301.2608 | NORMAL
298.8907 | 0.33333 | 296.113 | 0.51403 | 2 | 73773.932 | 10996.1632 | 9217.9693 | 2301.2608 | NORMAL
298.8907 | 0.33333 | 296.113 | 0.51403 | 2 | 90321.356 | 10942.5369 | 9351.5365 | 2301.2608 | NORMAL
298.8907 | 0.33333 | 296.113 | 0.51403 | 2 | 106868.78 | 10926.7901 | 9477.4865 | 2301.2608 | NORMAL
298.8907 | 0.33333 | 296.113 | 0.68163 | 1 | 57226.508 | 7362.0119 | 7807.2645 | 1531.3327 | NORMAL
298.8907 | 0.33333 | 296.113 | 0.68163 | 1 | 73773.932 | 7286.1268 | 7714.5626 | 1531.3327 | NORMAL
298.8907 | 0.33333 | 296.113 | 0.68163 | 1 | 90321.356 | 7250.5936 | 7650.1846 | 1531.3327 | NORMAL
298.8907 | 0.33333 | 296.113 | 0.68163 | 1 | 106868.78 | 7240.1597 | 7606.2871 | 1531.3327 | NORMAL
298.8907 | 0.33333 | 296.113 | 0.68163 | 2 | 57226.508 | 10756.7773 | 9930.378 | 2341.1262 | NORMAL
298.8907 | 0.33333 | 296.113 | 0.68163 | 2 | 73773.932 | 10645.9 | 9941.3533 | 2341.1262 | NORMAL
298.8907 | 0.33333 | 296.113 | 0.68163 | 2 | 90321.356 | 10593.9819 | 9966.6195 | 2341.1262 | NORMAL
298.8907 | 0.33333 | 296.113 | 0.68163 | 2 | 106868.78 | 10578.7366 | 10002.2772 | 2341.1262 | NORMAL
298.8907 | 0.33333 | 296.113 | 0.84923 | 1 | 57226.508 | 7096.4988 | 8235.1164 | 1505.538 | NORMAL
298.8907 | 0.33333 | 296.113 | 0.84923 | 1 | 73773.932 | 7023.3505 | 8079.8135 | 1505.538 | NORMAL
298.8907 | 0.33333 | 296.113 | 0.84923 | 1 | 90321.356 | 6989.0989 | 7963.898 | 1505.538 | NORMAL
298.8907 | 0.33333 | 296.113 | 0.84923 | 1 | 106868.78 | 6979.0412 | 7876.3998 | 1505.538 | NORMAL
298.8907 | 0.33333 | 296.113 | 0.84923 | 2 | 57226.508 | 10391.6661 | 10586.503 | 2326.8989 | NORMAL
298.8907 | 0.33333 | 296.113 | 0.84923 | 2 | 73773.932 | 10284.5523 | 10497.28 | 2326.8989 | NORMAL
298.8907 | 0.33333 | 296.113 | 0.84923 | 2 | 90321.356 | 10234.3964 | 10440.377 | 2326.8989 | NORMAL
298.8907 | 0.33333 | 296.113 | 0.84923 | 2 | 106868.78 | 10219.6686 | 10406.872 | 2326.8989 | NORMAL
298.8907 | 0.33333 | 300.7426 | 0.34644 | 1 | 57226.508 | 7932.8069 | 6322.9885 | 1522.8648 | NORMAL
298.8907 | 0.33333 | 300.7426 | 0.34644 | 1 | 73773.932 | 7999.6112 | 6476.1256 | 1536.5543 | NORMAL
298.8907 | 0.33333 | 300.7426 | 0.34644 | 1 | 90321.356 | 8085.4762 | 6633.2392 | 1546.3063 | NORMAL
298.8907 | 0.33333 | 300.7426 | 0.34644 | 1 | 106868.78 | 8181.2178 | 6789.9691 | 1553.1292 | NORMAL
298.8907 | 0.33333 | 300.7426 | 0.34644 | 2 | 57226.508 | 10762.1804 | 7551.152 | 2051.551 | NORMAL
298.8907 | 0.33333 | 300.7426 | 0.34644 | 2 | 73773.932 | 10852.8116 | 7891.0365 | 2069.9931 | NORMAL
298.8907 | 0.33333 | 300.7426 | 0.34644 | 2 | 90321.356 | 10969.3019 | 8216.2449 | 2083.1306 | NORMAL
298.8907 | 0.33333 | 300.7426 | 0.34644 | 2 | 106868.78 | 11099.1914 | 8524.7942 | 2092.3222 | NORMAL
298.8907 | 0.33333 | 300.7426 | 0.51403 | 1 | 57226.508 | 7607.7523 | 7348.5686 | 1568.8344 | NORMAL
298.8907 | 0.33333 | 300.7426 | 0.51403 | 1 | 73773.932 | 7671.8192 | 7367.0034 | 1582.9372 | NORMAL
298.8907 | 0.33333 | 300.7426 | 0.51403 | 1 | 90321.356 | 7754.1658 | 7409.2499 | 1592.9836 | NORMAL
298.8907 | 0.33333 | 300.7426 | 0.51403 | 1 | 106868.78 | 7845.9843 | 7466.2173 | 1600.0124 | NORMAL
298.8907 | 0.33333 | 300.7426 | 0.51403 | 2 | 57226.508 | 10969.8663 | 9047.4087 | 2330.1223 | NORMAL
298.8907 | 0.33333 | 300.7426 | 0.51403 | 2 | 73773.932 | 11062.2465 | 9225.7812 | 2351.0685 | NORMAL
298.8907 | 0.33333 | 300.7426 | 0.51403 | 2 | 90321.356 | 11180.9847 | 9414.7583 | 2365.99 | NORMAL
298.8907 | 0.33333 | 300.7426 | 0.51403 | 2 | 106868.78 | 11313.3808 | 9607.1468 | 2376.4297 | NORMAL
298.8907 | 0.33333 | 300.7426 | 0.68163 | 1 | 57226.508 | 7268.7023 | 8051.0882 | 1550.5382 | NORMAL
298.8907 | 0.33333 | 300.7426 | 0.68163 | 1 | 73773.932 | 7329.914 | 7978.6268 | 1564.4764 | NORMAL
298.8907 | 0.33333 | 300.7426 | 0.68163 | 1 | 90321.356 | 7408.5907 | 7943.4634 | 1574.4057 | NORMAL
298.8907 | 0.33333 | 300.7426 | 0.68163 | 1 | 106868.78 | 7496.3171 | 7933.0082 | 1581.3525 | NORMAL
298.8907 | 0.33333 | 300.7426 | 0.68163 | 2 | 57226.508 | 10620.4408 | 10083.1884 | 2370.4878 | NORMAL
298.8907 | 0.33333 | 300.7426 | 0.68163 | 2 | 73773.932 | 10709.8784 | 10125.046 | 2391.7968 | NORMAL
298.8907 | 0.33333 | 300.7426 | 0.68163 | 2 | 90321.356 | 10824.8344 | 10197.5822 | 2406.9768 | NORMAL
298.8907 | 0.33333 | 300.7426 | 0.68163 | 2 | 106868.78 | 10953.0133 | 10288.7742 | 2417.5973 | NORMAL
298.8907 | 0.33333 | 300.7426 | 0.84923 | 1 | 57226.508 | 7006.5544 | 8561.9592 | 1524.4199 | NORMAL
298.8907 | 0.33333 | 300.7426 | 0.84923 | 1 | 73773.932 | 7065.5585 | 8425.8295 | 1538.1234 | NORMAL
298.8907 | 0.33333 | 300.7426 | 0.84923 | 1 | 90321.356 | 7141.3977 | 8336.5747 | 1547.8854 | NORMAL
298.8907 | 0.33333 | 300.7426 | 0.84923 | 1 | 106868.78 | 7225.9603 | 8279.0402 | 1554.7153 | NORMAL
298.8907 | 0.33333 | 300.7426 | 0.84923 | 2 | 57226.508 | 10259.9572 | 10872.7797 | 2356.082 | NORMAL
298.8907 | 0.33333 | 300.7426 | 0.84923 | 2 | 73773.932 | 10346.3591 | 10812.4141 | 2377.2616 | NORMAL
298.8907 | 0.33333 | 300.7426 | 0.84923 | 2 | 90321.356 | 10457.4132 | 10797.8669 | 2392.3493 | NORMAL
298.8907 | 0.33333 | 300.7426 | 0.84923 | 2 | 106868.78 | 10581.2414 | 10813.2259 | 2402.9053 | NORMAL
298.8907 | 0.33333 | 305.3722 | 0.34644 | 1 | 57226.508 | 8424.3791 | 6500.721 | 1561.0429 | NORMAL
298.8907 | 0.33333 | 305.3722 | 0.34644 | 1 | 73773.932 | 8629.7166 | 6689.41 | 1561.25 | NORMAL
298.8907 | 0.33333 | 305.3722 | 0.34644 | 1 | 90321.356 | 8834.1566 | 6896.574 | 1557.1725 | NORMAL
298.8907 | 0.33333 | 305.3722 | 0.34644 | 1 | 106868.78 | 9034.0225 | 7111.9724 | 1549.666 | NORMAL
298.8907 | 0.33333 | 305.3722 | 0.34644 | 2 | 57226.508 | 11429.0804 | 7647.0647 | 2102.9833 | NORMAL
298.8907 | 0.33333 | 305.3722 | 0.34644 | 2 | 73773.932 | 11707.655 | 8040.5011 | 2103.2622 | NORMAL
298.8907 | 0.33333 | 305.3722 | 0.34644 | 2 | 90321.356 | 11985.0122 | 8444.9111 | 2097.7692 | NORMAL
298.8907 | 0.33333 | 305.3722 | 0.34644 | 2 | 106868.78 | 12256.1637 | 8848.4683 | 2087.6568 | NORMAL
298.8907 | 0.33333 | 305.3722 | 0.51403 | 1 | 57226.508 | 8079.1818 | 7675.0618 | 1608.165 | NORMAL
298.8907 | 0.33333 | 305.3722 | 0.51403 | 1 | 73773.932 | 8276.1054 | 7725.1418 | 1608.3783 | NORMAL
298.8907 | 0.33333 | 305.3722 | 0.51403 | 1 | 90321.356 | 8472.1683 | 7809.5275 | 1604.1778 | NORMAL
298.8907 | 0.33333 | 305.3722 | 0.51403 | 1 | 106868.78 | 8663.8445 | 7914.3287 | 1596.4447 | NORMAL
298.8907 | 0.33333 | 305.3722 | 0.51403 | 2 | 57226.508 | 11649.636 | 9332.1744 | 2388.5384 | NORMAL
298.8907 | 0.33333 | 305.3722 | 0.51403 | 2 | 73773.932 | 11933.5865 | 9558.8253 | 2388.8552 | NORMAL
298.8907 | 0.33333 | 305.3722 | 0.51403 | 2 | 90321.356 | 12216.296 | 9815.0122 | 2382.6163 | NORMAL
298.8907 | 0.33333 | 305.3722 | 0.51403 | 2 | 106868.78 | 12492.6801 | 10085.7114 | 2371.1307 | NORMAL
298.8907 | 0.33333 | 305.3722 | 0.68163 | 1 | 57226.508 | 7719.1219 | 8479.2102 | 1589.4101 | NORMAL
298.8907 | 0.33333 | 305.3722 | 0.68163 | 1 | 73773.932 | 7907.2693 | 8436.1911 | 1589.6209 | NORMAL
298.8907 | 0.33333 | 305.3722 | 0.68163 | 1 | 90321.356 | 8094.5944 | 8438.9951 | 1585.4693 | NORMAL
298.8907 | 0.33333 | 305.3722 | 0.68163 | 1 | 106868.78 | 8277.7283 | 8470.7411 | 1577.8265 | NORMAL
298.8907 | 0.33333 | 305.3722 | 0.68163 | 2 | 57226.508 | 11278.5576 | 10518.645 | 2429.9158 | NORMAL
298.8907 | 0.33333 | 305.3722 | 0.68163 | 2 | 73773.932 | 11553.4633 | 10604.8797 | 2430.2381 | NORMAL
298.8907 | 0.33333 | 305.3722 | 0.68163 | 2 | 90321.356 | 11827.1677 | 10736.7689 | 2423.8911 | NORMAL
298.8907 | 0.33333 | 305.3722 | 0.68163 | 2 | 106868.78 | 12094.7481 | 10895.519 | 2412.2065 | NORMAL
298.8907 | 0.33333 | 305.3722 | 0.84923 | 1 | 57226.508 | 7440.7296 | 9062.3889 | 1562.6371 | NORMAL
298.8907 | 0.33333 | 305.3722 | 0.84923 | 1 | 73773.932 | 7622.0914 | 8954.3208 | 1562.8444 | NORMAL
298.8907 | 0.33333 | 305.3722 | 0.84923 | 1 | 90321.356 | 7802.6605 | 8900.5023 | 1558.7627 | NORMAL
298.8907 | 0.33333 | 305.3722 | 0.84923 | 1 | 106868.78 | 7979.1896 | 8881.7786 | 1551.2486 | NORMAL
298.8907 | 0.33333 | 305.3722 | 0.84923 | 2 | 57226.508 | 10895.7359 | 11422.3838 | 2415.1489 | NORMAL
298.8907 | 0.33333 | 305.3722 | 0.84923 | 2 | 73773.932 | 11161.3107 | 11403.8682 | 2415.4693 | NORMAL
298.8907 | 0.33333 | 305.3722 | 0.84923 | 2 | 90321.356 | 11425.7248 | 11443.827 | 2409.1608 | NORMAL
298.8907 | 0.33333 | 305.3722 | 0.84923 | 2 | 106868.78 | 11684.2229 | 11520.1771 | 2397.5473 | NORMAL
298.8907 | 0.66667 | 291.4833 | 0.34644 | 1 | 57226.508 | 7901.6319 | 3845.6916 | 1504.0021 | NORMAL
298.8907 | 0.66667 | 291.4833 | 0.34644 | 1 | 73773.932 | 7903.7793 | 4233.3453 | 1507.7987 | NORMAL
298.8907 | 0.66667 | 291.4833 | 0.34644 | 1 | 90321.356 | 7909.9202 | 4570.3718 | 1513.1806 | NORMAL
298.8907 | 0.66667 | 291.4833 | 0.34644 | 1 | 106868.78 | 7918.5091 | 4862.3245 | 1517.6846 | NORMAL
298.8907 | 0.66667 | 291.4833 | 0.34644 | 2 | 57226.508 | 10719.8863 | 4951.4126 | 2026.1399 | NORMAL
298.8907 | 0.66667 | 291.4833 | 0.34644 | 2 | 73773.932 | 10722.7997 | 5562.7718 | 2031.2546 | NORMAL
298.8907 | 0.66667 | 291.4833 | 0.34644 | 2 | 90321.356 | 10731.1308 | 6089.1194 | 2038.5048 | NORMAL
298.8907 | 0.66667 | 291.4833 | 0.34644 | 2 | 106868.78 | 10742.7831 | 6520.8704 | 2044.5726 | NORMAL
298.8907 | 0.66667 | 291.4833 | 0.51403 | 1 | 57226.508 | 7577.8547 | 4086.7509 | 1549.4024 | NORMAL
298.8907 | 0.66667 | 291.4833 | 0.51403 | 1 | 73773.932 | 7579.9142 | 4387.7097 | 1553.3136 | NORMAL
298.8907 | 0.66667 | 291.4833 | 0.51403 | 1 | 90321.356 | 7585.8034 | 4652.0732 | 1558.8579 | NORMAL
298.8907 | 0.66667 | 291.4833 | 0.51403 | 1 | 106868.78 | 7594.0404 | 4883.4539 | 1563.498 | NORMAL
298.8907 | 0.66667 | 291.4833 | 0.51403 | 2 | 57226.508 | 10926.756 | 5406.807 | 2301.2608 | NORMAL
298.8907 | 0.66667 | 291.4833 | 0.51403 | 2 | 73773.932 | 10929.7256 | 5923.139 | 2307.0699 | NORMAL
298.8907 | 0.66667 | 291.4833 | 0.51403 | 2 | 90321.356 | 10938.2175 | 6372.9122 | 2315.3047 | NORMAL
298.8907 | 0.66667 | 291.4833 | 0.51403 | 2 | 106868.78 | 10950.0947 | 6763.404 | 2322.1963 | NORMAL
298.8907 | 0.66667 | 291.4833 | 0.68163 | 1 | 57226.508 | 7240.1371 | 4247.3836 | 1531.3327 | NORMAL
298.8907 | 0.66667 | 291.4833 | 0.68163 | 1 | 73773.932 | 7242.1048 | 4490.954 | 1535.1984 | NORMAL
298.8907 | 0.66667 | 291.4833 | 0.68163 | 1 | 90321.356 | 7247.7315 | 4706.7238 | 1540.678 | NORMAL
298.8907 | 0.66667 | 291.4833 | 0.68163 | 1 | 106868.78 | 7255.6015 | 4896.734 | 1545.2639 | NORMAL
298.8907 | 0.66667 | 291.4833 | 0.68163 | 2 | 57226.508 | 10578.7037 | 5648.1409 | 2341.1262 | NORMAL
298.8907 | 0.66667 | 291.4833 | 0.68163 | 2 | 73773.932 | 10581.5787 | 6076.5481 | 2347.036 | NORMAL
298.8907 | 0.66667 | 291.4833 | 0.68163 | 2 | 90321.356 | 10589.8 | 6452.5115 | 2355.4134 | NORMAL
298.8907 | 0.66667 | 291.4833 | 0.68163 | 2 | 106868.78 | 10601.2989 | 6781.3113 | 2362.4244 | NORMAL
298.8907 | 0.66667 | 291.4833 | 0.84923 | 1 | 57226.508 | 6979.0195 | 4367.669 | 1505.538 | NORMAL
298.8907 | 0.66667 | 291.4833 | 0.84923 | 1 | 73773.932 | 6980.9162 | 4572.0269 | 1509.3385 | NORMAL
298.8907 | 0.66667 | 291.4833 | 0.84923 | 1 | 90321.356 | 6986.34 | 4754.5326 | 1514.7259 | NORMAL
298.8907 | 0.66667 | 291.4833 | 0.84923 | 1 | 106868.78 | 6993.9261 | 4916.0418 | 1519.2346 | NORMAL
298.8907 | 0.66667 | 291.4833 | 0.84923 | 2 | 57226.508 | 10219.6367 | 5829.7921 | 2326.8989 | NORMAL
298.8907 | 0.66667 | 291.4833 | 0.84923 | 2 | 73773.932 | 10222.4142 | 6193.5174 | 2332.7728 | NORMAL
298.8907 | 0.66667 | 291.4833 | 0.84923 | 2 | 90321.356 | 10230.3565 | 6514.7646 | 2341.0993 | NORMAL
298.8907 | 0.66667 | 291.4833 | 0.84923 | 2 | 106868.78 | 10241.4651 | 6797.0918 | 2348.0677 | NORMAL
298.8907 | 0.66667 | 296.113 | 0.34644 | 1 | 57226.508 | 8328.4377 | 3672.4387 | 1559.1269 | NORMAL
298.8907 | 0.66667 | 296.113 | 0.34644 | 1 | 73773.932 | 8394.5633 | 4056.4271 | 1560.5882 | NORMAL
298.8907 | 0.66667 | 296.113 | 0.34644 | 1 | 90321.356 | 8456.3983 | 4411.3234 | 1561.4008 | NORMAL
298.8907 | 0.66667 | 296.113 | 0.34644 | 1 | 106868.78 | 8514.1659 | 4735.9135 | 1561.7263 | NORMAL
298.8907 | 0.66667 | 296.113 | 0.34644 | 2 | 57226.508 | 11298.9198 | 4630.639 | 2100.4021 | NORMAL
298.8907 | 0.66667 | 296.113 | 0.34644 | 2 | 73773.932 | 11388.6302 | 5237.0949 | 2102.3707 | NORMAL
298.8907 | 0.66667 | 296.113 | 0.34644 | 2 | 90321.356 | 11472.5198 | 5795.533 | 2103.4655 | NORMAL
298.8907 | 0.66667 | 296.113 | 0.34644 | 2 | 106868.78 | 11550.8913 | 6302.862 | 2103.9039 | NORMAL
298.8907 | 0.66667 | 296.113 | 0.51403 | 1 | 57226.508 | 7987.1717 | 3999.5924 | 1606.1911 | NORMAL
298.8907 | 0.66667 | 296.113 | 0.51403 | 1 | 73773.932 | 8050.5877 | 4298.0752 | 1607.6966 | NORMAL
298.8907 | 0.66667 | 296.113 | 0.51403 | 1 | 90321.356 | 8109.889 | 4576.3395 | 1608.5338 | NORMAL
298.8907 | 0.66667 | 296.113 | 0.51403 | 1 | 106868.78 | 8165.2896 | 4832.888 | 1608.8691 | NORMAL
298.8907 | 0.66667 | 296.113 | 0.51403 | 2 | 57226.508 | 11516.9636 | 5188.2114 | 2385.6067 | NORMAL
298.8907 | 0.66667 | 296.113 | 0.51403 | 2 | 73773.932 | 11608.4052 | 5699.6835 | 2387.8426 | NORMAL
298.8907 | 0.66667 | 296.113 | 0.51403 | 2 | 90321.356 | 11693.9137 | 6172.952 | 2389.086 | NORMAL
298.8907 | 0.66667 | 296.113 | 0.51403 | 2 | 106868.78 | 11773.7975 | 6606.4154 | 2389.584 | NORMAL
298.8907 | 0.66667 | 296.113 | 0.68163 | 1 | 57226.508 | 7631.2123 | 4217.6484 | 1587.4592 | NORMAL
298.8907 | 0.66667 | 296.113 | 0.68163 | 1 | 73773.932 | 7691.8021 | 4459.6777 | 1588.9471 | NORMAL
298.8907 | 0.66667 | 296.113 | 0.68163 | 1 | 90321.356 | 7748.4606 | 4687.752 | 1589.7745 | NORMAL
298.8907 | 0.66667 | 296.113 | 0.68163 | 1 | 106868.78 | 7801.3921 | 4899.5832 | 1590.1059 | NORMAL
298.8907 | 0.66667 | 296.113 | 0.68163 | 2 | 57226.508 | 11150.1112 | 5516.7566 | 2426.9333 | NORMAL
298.8907 | 0.66667 | 296.113 | 0.68163 | 2 | 73773.932 | 11238.6402 | 5941.5593 | 2429.208 | NORMAL
298.8907 | 0.66667 | 296.113 | 0.68163 | 2 | 90321.356 | 11321.4249 | 6337.1792 | 2430.4729 | NORMAL
298.8907 | 0.66667 | 296.113 | 0.68163 | 2 | 106868.78 | 11398.7642 | 6701.6401 | 2430.9796 | NORMAL
298.8907 | 0.66667 | 296.113 | 0.84923 | 1 | 57226.508 | 7355.9905 | 4377.7883 | 1560.7191 | NORMAL
298.8907 | 0.66667 | 296.113 | 0.84923 | 1 | 73773.932 | 7414.3951 | 4581.2405 | 1562.1819 | NORMAL
298.8907 | 0.66667 | 296.113 | 0.84923 | 1 | 90321.356 | 7469.0101 | 4775.2099 | 1562.9954 | NORMAL
298.8907 | 0.66667 | 296.113 | 0.84923 | 1 | 106868.78 | 7520.0327 | 4956.6799 | 1563.3212 | NORMAL
298.8907 | 0.66667 | 296.113 | 0.84923 | 2 | 57226.508 | 10771.6493 | 5763.0803 | 2412.1845 | NORMAL
298.8907 | 0.66667 | 296.113 | 0.84923 | 2 | 73773.932 | 10857.1734 | 6124.2509 | 2414.4454 | NORMAL
298.8907 | 0.66667 | 296.113 | 0.84923 | 2 | 90321.356 | 10937.1482 | 6463.2235 | 2415.7027 | NORMAL
298.8907 | 0.66667 | 296.113 | 0.84923 | 2 | 106868.78 | 11011.8624 | 6777.2197 | 2416.2062 | NORMAL
298.8907 | 0.66667 | 300.7426 | 0.34644 | 1 | 57226.508 | 9631.7938 | 3726.4458 | 1509.1266 | NORMAL
298.8907 | 0.66667 | 300.7426 | 0.34644 | 1 | 73773.932 | 9752.2695 | 4139.5083 | 1504.5713 | NORMAL
298.8907 | 0.66667 | 300.7426 | 0.34644 | 1 | 90321.356 | 9862.8847 | 4540.1928 | 1504.5713 | NORMAL
298.8907 | 0.66667 | 300.7426 | 0.34644 | 1 | 106868.78 | 9965.4458 | 4921.7149 | 1504.5713 | NORMAL
298.8907 | 0.66667 | 300.7426 | 0.34644 | 2 | 57226.508 | 13067.1405 | 4645.6013 | 2033.0435 | NORMAL
298.8907 | 0.66667 | 300.7426 | 0.34644 | 2 | 73773.932 | 13230.586 | 5297.7654 | 2026.9067 | NORMAL
298.8907 | 0.66667 | 300.7426 | 0.34644 | 2 | 90321.356 | 13380.654 | 5930.7318 | 2026.9067 | NORMAL
298.8907 | 0.66667 | 300.7426 | 0.34644 | 2 | 106868.78 | 13519.7953 | 6532.524 | 2026.9067 | NORMAL
298.8907 | 0.66667 | 300.7426 | 0.51403 | 1 | 57226.508 | 9237.1215 | 4114.106 | 1554.6816 | NORMAL
298.8907 | 0.66667 | 300.7426 | 0.51403 | 1 | 73773.932 | 9352.6606 | 4437.4679 | 1549.9888 | NORMAL
298.8907 | 0.66667 | 300.7426 | 0.51403 | 1 | 90321.356 | 9458.7432 | 4753.5897 | 1549.9888 | NORMAL
298.8907 | 0.66667 | 300.7426 | 0.51403 | 1 | 106868.78 | 9557.1018 | 5055.96 | 1549.9888 | NORMAL
298.8907 | 0.66667 | 300.7426 | 0.51403 | 2 | 57226.508 | 13319.307 | 5278.5719 | 2309.1017 | NORMAL
298.8907 | 0.66667 | 300.7426 | 0.51403 | 2 | 73773.932 | 13485.9066 | 5829.1866 | 2302.1317 | NORMAL
298.8907 | 0.66667 | 300.7426 | 0.51403 | 2 | 90321.356 | 13638.8706 | 6363.6431 | 2302.1317 | NORMAL
298.8907 | 0.66667 | 300.7426 | 0.51403 | 2 | 106868.78 | 13780.697 | 6872.8004 | 2302.1317 | NORMAL
298.8907 | 0.66667 | 300.7426 | 0.68163 | 1 | 57226.508 | 8825.4564 | 4373.6851 | 1536.5504 | NORMAL
298.8907 | 0.66667 | 300.7426 | 0.68163 | 1 | 73773.932 | 8935.8464 | 4638.4277 | 1531.9123 | NORMAL
298.8907 | 0.66667 | 300.7426 | 0.68163 | 1 | 90321.356 | 9037.2012 | 4900.5161 | 1531.9123 | NORMAL
298.8907 | 0.66667 | 300.7426 | 0.68163 | 1 | 106868.78 | 9131.1763 | 5152.8281 | 1531.9123 | NORMAL
298.8907 | 0.66667 | 300.7426 | 0.68163 | 2 | 57226.508 | 12895.0442 | 5668.4526 | 2349.103 | NORMAL
298.8907 | 0.66667 | 300.7426 | 0.68163 | 2 | 73773.932 | 13056.3371 | 6128.2418 | 2342.0122 | NORMAL
298.8907 | 0.66667 | 300.7426 | 0.68163 | 2 | 90321.356 | 13204.4286 | 6577.2295 | 2342.0122 | NORMAL
298.8907 | 0.66667 | 300.7426 | 0.68163 | 2 | 106868.78 | 13341.7374 | 7006.4304 | 2342.0122 | NORMAL
298.8907 | 0.66667 | 300.7426 | 0.84923 | 1 | 57226.508 | 8507.1638 | 4563.3727 | 1510.6678 | NORMAL
298.8907 | 0.66667 | 300.7426 | 0.84923 | 1 | 73773.932 | 8613.5725 | 4788.2381 | 1506.1078 | NORMAL
298.8907 | 0.66667 | 300.7426 | 0.84923 | 1 | 90321.356 | 8711.272 | 5014.0041 | 1506.1078 | NORMAL
298.8907 | 0.66667 | 300.7426 | 0.84923 | 1 | 106868.78 | 8801.8578 | 5232.8903 | 1506.1078 | NORMAL
298.8907 | 0.66667 | 300.7426 | 0.84923 | 2 | 57226.508 | 12457.355 | 5961.3871 | 2334.8272 | NORMAL
298.8907 | 0.66667 | 300.7426 | 0.84923 | 2 | 73773.932 | 12613.1733 | 6355.0231 | 2327.7796 | NORMAL
298.8907 | 0.66667 | 300.7426 | 0.84923 | 2 | 90321.356 | 12756.2382 | 6742.8363 | 2327.7796 | NORMAL
298.8907 | 0.66667 | 300.7426 | 0.84923 | 2 | 106868.78 | 12888.8864 | 7115.2666 | 2327.7796 | NORMAL
298.8907 | 0.66667 | 305.3722 | 0.34644 | 1 | 57226.508 | 11824.6156 | 3900.8339 | 1504.5713 | NORMAL
298.8907 | 0.66667 | 305.3722 | 0.34644 | 1 | 73773.932 | 11988.3813 | 4363.9543 | 1504.5713 | NORMAL
298.8907 | 0.66667 | 305.3722 | 0.34644 | 1 | 90321.356 | 12139.9123 | 4830.5542 | 1504.5713 | NORMAL
298.8907 | 0.66667 | 305.3722 | 0.34644 | 1 | 106868.78 | 12280.6265 | 5290.1667 | 1504.5713 | NORMAL
298.8907 | 0.66667 | 305.3722 | 0.34644 | 2 | 57226.508 | 16042.0703 | 4835.6578 | 2026.9067 | NORMAL
298.8907 | 0.66667 | 305.3722 | 0.34644 | 2 | 73773.932 | 16264.2459 | 5568.2678 | 2026.9067 | NORMAL
298.8907 | 0.66667 | 305.3722 | 0.34644 | 2 | 90321.356 | 16469.8231 | 6310.5011 | 2026.9067 | NORMAL
298.8907 | 0.66667 | 305.3722 | 0.34644 | 2 | 106868.78 | 16660.7255 | 7044.519 | 2026.9067 | NORMAL
298.8907 | 0.66667 | 305.3722 | 0.51403 | 1 | 57226.508 | 11340.0903 | 4337.6341 | 1549.9888 | NORMAL
298.8907 | 0.66667 | 305.3722 | 0.51403 | 1 | 73773.932 | 11497.1455 | 4702.2441 | 1549.9888 | NORMAL
298.8907 | 0.66667 | 305.3722 | 0.51403 | 1 | 90321.356 | 11642.4674 | 5071.5582 | 1549.9888 | NORMAL
298.8907 | 0.66667 | 305.3722 | 0.51403 | 1 | 106868.78 | 11777.4157 | 5435.7069 | 1549.9888 | NORMAL
298.8907 | 0.66667 | 305.3722 | 0.51403 | 2 | 57226.508 | 16351.6463 | 5533.2119 | 2302.1317 | NORMAL
298.8907 | 0.66667 | 305.3722 | 0.51403 | 2 | 73773.932 | 16578.1093 | 6150.7861 | 2302.1317 | NORMAL
298.8907 | 0.66667 | 305.3722 | 0.51403 | 2 | 90321.356 | 16787.6537 | 6772.9336 | 2302.1317 | NORMAL
298.8907 | 0.66667 | 305.3722 | 0.51403 | 2 | 106868.78 | 16982.2401 | 7385.5164 | 2302.1317 | NORMAL
298.8907 | 0.66667 | 305.3722 | 0.68163 | 1 | 57226.508 | 10834.7034 | 4631.5122 | 1531.9123 | NORMAL
298.8907 | 0.66667 | 305.3722 | 0.68163 | 1 | 73773.932 | 10984.7593 | 4932.8475 | 1531.9123 | NORMAL
298.8907 | 0.66667 | 305.3722 | 0.68163 | 1 | 90321.356 | 11123.6047 | 5241.9329 | 1531.9123 | NORMAL
298.8907 | 0.66667 | 305.3722 | 0.68163 | 1 | 106868.78 | 11252.5389 | 5548.3896 | 1531.9123 | NORMAL
298.8907 | 0.66667 | 305.3722 | 0.68163 | 2 | 57226.508 | 15830.7937 | 5972.9031 | 2342.0122 | NORMAL
298.8907 | 0.66667 | 305.3722 | 0.68163 | 2 | 73773.932 | 16050.0432 | 6490.9021 | 2342.0122 | NORMAL
298.8907 | 0.66667 | 305.3722 | 0.68163 | 2 | 90321.356 | 16252.9129 | 7015.0336 | 2342.0122 | NORMAL
298.8907 | 0.66667 | 305.3722 | 0.68163 | 2 | 106868.78 | 16441.3011 | 7531.6233 | 2342.0122 | NORMAL
298.8907 | 0.66667 | 305.3722 | 0.84923 | 1 | 57226.508 | 10443.9467 | 4846.0383 | 1506.1078 | NORMAL
298.8907 | 0.66667 | 305.3722 | 0.84923 | 1 | 73773.932 | 10588.5908 | 5104.6623 | 1506.1078 | NORMAL
298.8907 | 0.66667 | 305.3722 | 0.84923 | 1 | 90321.356 | 10722.4287 | 5373.8284 | 1506.1078 | NORMAL
298.8907 | 0.66667 | 305.3722 | 0.84923 | 1 | 106868.78 | 10846.7128 | 5642.5349 | 1506.1078 | NORMAL
298.8907 | 0.66667 | 305.3722 | 0.84923 | 2 | 57226.508 | 15293.4581 | 6304.2752 | 2327.7796 | NORMAL
298.8907 | 0.66667 | 305.3722 | 0.84923 | 2 | 73773.932 | 15505.2657 | 6750.7106 | 2327.7796 | NORMAL
298.8907 | 0.66667 | 305.3722 | 0.84923 | 2 | 90321.356 | 15701.2495 | 7206.3738 | 2327.7796 | NORMAL
298.8907 | 0.66667 | 305.3722 | 0.84923 | 2 | 106868.78 | 15883.2434 | 7657.1438 | 2327.7796 | NORMAL
298.8907 | 1 | 291.4833 | 0.34644 | 1 | 57226.508 | 8418.9398 | 2025.8372 | 1560.9689 | NORMAL
298.8907 | 1 | 291.4833 | 0.34644 | 1 | 73773.932 | 8418.9398 | 2531.8369 | 1560.9689 | NORMAL
298.8907 | 1 | 291.4833 | 0.34644 | 1 | 90321.356 | 8418.9398 | 2988.1936 | 1560.9689 | NORMAL
298.8907 | 1 | 291.4833 | 0.34644 | 1 | 106868.78 | 8418.9398 | 3396.8549 | 1560.9689 | NORMAL
298.8907 | 1 | 291.4833 | 0.34644 | 2 | 57226.508 | 11421.7011 | 2862.4436 | 2102.8836 | NORMAL
298.8907 | 1 | 291.4833 | 0.34644 | 2 | 73773.932 | 11421.7011 | 3603.7097 | 2102.8836 | NORMAL
298.8907 | 1 | 291.4833 | 0.34644 | 2 | 90321.356 | 11421.7011 | 4273.6519 | 2102.8836 | NORMAL
298.8907 | 1 | 291.4833 | 0.34644 | 2 | 106868.78 | 11421.7011 | 4871.1722 | 2102.8836 | NORMAL
298.8907 | 1 | 291.4833 | 0.51403 | 1 | 57226.508 | 8073.9654 | 1872.1609 | 1608.0888 | NORMAL
298.8907 | 1 | 291.4833 | 0.51403 | 1 | 73773.932 | 8073.9654 | 2324.3791 | 1608.0888 | NORMAL
298.8907 | 1 | 291.4833 | 0.51403 | 1 | 90321.356 | 8073.9654 | 2730.8543 | 1608.0888 | NORMAL
298.8907 | 1 | 291.4833 | 0.51403 | 1 | 106868.78 | 8073.9654 | 3095.3311 | 1608.0888 | NORMAL
298.8907 | 1 | 291.4833 | 0.51403 | 2 | 57226.508 | 11642.1143 | 2778.7835 | 2388.4251 | NORMAL
298.8907 | 1 | 291.4833 | 0.51403 | 2 | 73773.932 | 11642.1143 | 3467.8008 | 2388.4251 | NORMAL
298.8907 | 1 | 291.4833 | 0.51403 | 2 | 90321.356 | 11642.1143 | 4088.8225 | 2388.4251 | NORMAL
298.8907 | 1 | 291.4833 | 0.51403 | 2 | 106868.78 | 11642.1143 | 4645.1945 | 2388.4251 | NORMAL
298.8907 | 1 | 291.4833 | 0.68163 | 1 | 57226.508 | 7714.138 | 1757.4396 | 1589.3347 | NORMAL
298.8907 | 1 | 291.4833 | 0.68163 | 1 | 73773.932 | 7714.138 | 2175.1927 | 1589.3347 | NORMAL
298.8907 | 1 | 291.4833 | 0.68163 | 1 | 90321.356 | 7714.138 | 2549.9523 | 1589.3347 | NORMAL
298.8907 | 1 | 291.4833 | 0.68163 | 1 | 106868.78 | 7714.138 | 2885.9979 | 1589.3347 | NORMAL
298.8907 | 1 | 291.4833 | 0.68163 | 2 | 57226.508 | 11271.2755 | 2620.4149 | 2429.8005 | NORMAL
298.8907 | 1 | 291.4833 | 0.68163 | 2 | 73773.932 | 11271.2755 | 3254.8837 | 2429.8005 | NORMAL
298.8907 | 1 | 291.4833 | 0.68163 | 2 | 90321.356 | 11271.2755 | 3825.3314 | 2429.8005 | NORMAL
298.8907 | 1 | 291.4833 | 0.68163 | 2 | 106868.78 | 11271.2755 | 4336.8212 | 2429.8005 | NORMAL
298.8907 | 1 | 291.4833 | 0.84923 | 1 | 57226.508 | 7435.9254 | 1677.2551 | 1562.563 | NORMAL
298.8907 | 1 | 291.4833 | 0.84923 | 1 | 73773.932 | 7435.9254 | 2072.3475 | 1562.563 | NORMAL
298.8907 | 1 | 291.4833 | 0.84923 | 1 | 90321.356 | 7435.9254 | 2426.3582 | 1562.563 | NORMAL
298.8907 | 1 | 291.4833 | 0.84923 | 1 | 106868.78 | 7435.9254 | 2743.7566 | 1562.563 | NORMAL
298.8907 | 1 | 291.4833 | 0.84923 | 2 | 57226.508 | 10888.701 | 2493.48 | 2415.0344 | NORMAL
298.8907 | 1 | 291.4833 | 0.84923 | 2 | 73773.932 | 10888.701 | 3088.9772 | 2415.0344 | NORMAL
298.8907 | 1 | 291.4833 | 0.84923 | 2 | 90321.356 | 10888.701 | 3623.5048 | 2415.0344 | NORMAL
298.8907 | 1 | 291.4833 | 0.84923 | 2 | 106868.78 | 10888.701 | 4102.8276 | 2415.0344 | NORMAL
298.8907 | 1 | 296.113 | 0.34644 | 1 | 57226.508 | 10008.3917 | 1933.9846 | 1504.5713 | NORMAL
298.8907 | 1 | 296.113 | 0.34644 | 1 | 73773.932 | 10008.3917 | 2460.5217 | 1504.5713 | NORMAL
298.8907 | 1 | 296.113 | 0.34644 | 1 | 90321.356 | 10008.3917 | 2952.5025 | 1504.5713 | NORMAL
298.8907 | 1 | 296.113 | 0.34644 | 1 | 106868.78 | 10008.3917 | 3408.0663 | 1504.5713 | NORMAL
298.8907 | 1 | 296.113 | 0.34644 | 2 | 57226.508 | 13578.0587 | 2728.8957 | 2026.9067 | NORMAL
298.8907 | 1 | 296.113 | 0.34644 | 2 | 73773.932 | 13578.0587 | 3504.1992 | 2026.9067 | NORMAL
298.8907 | 1 | 296.113 | 0.34644 | 2 | 90321.356 | 13578.0587 | 4234.9596 | 2026.9067 | NORMAL
298.8907 | 1 | 296.113 | 0.34644 | 2 | 106868.78 | 13578.0587 | 4913.172 | 2026.9067 | NORMAL
298.8907 | 1 | 296.113 | 0.51403 | 1 | 57226.508 | 9598.288 | 1789.806 | 1549.9888 | NORMAL
298.8907 | 1 | 296.113 | 0.51403 | 1 | 73773.932 | 9598.288 | 2258.7422 | 1549.9888 | NORMAL
298.8907 | 1 | 296.113 | 0.51403 | 1 | 90321.356 | 9598.288 | 2693.2072 | 1549.9888 | NORMAL
298.8907 | 1 | 296.113 | 0.51403 | 1 | 106868.78 | 9598.288 | 3094.011 | 1549.9888 | NORMAL
298.8907 | 1 | 296.113 | 0.51403 | 2 | 57226.508 | 13840.0847 | 2653.5822 | 2302.1317 | NORMAL
298.8907 | 1 | 296.113 | 0.51403 | 2 | 73773.932 | 13840.0847 | 3369.9548 | 2302.1317 | NORMAL
298.8907 | 1 | 296.113 | 0.51403 | 2 | 90321.356 | 13840.0847 | 4038.0901 | 2302.1317 | NORMAL
298.8907 | 1 | 296.113 | 0.51403 | 2 | 106868.78 | 13840.0847 | 4656.3299 | 2302.1317 | NORMAL
298.8907 | 1 | 296.113 | 0.68163 | 1 | 57226.508 | 9170.527 | 1681.3403 | 1531.9123 | NORMAL
298.8907 | 1 | 296.113 | 0.68163 | 1 | 73773.932 | 9170.527 | 2113.9654 | 1531.9123 | NORMAL
298.8907 | 1 | 296.113 | 0.68163 | 1 | 90321.356 | 9170.527 | 2513.1499 | 1531.9123 | NORMAL
298.8907 | 1 | 296.113 | 0.68163 | 1 | 106868.78 | 9170.527 | 2880.6192 | 1531.9123 | NORMAL
298.8907 | 1 | 296.113 | 0.68163 | 2 | 57226.508 | 13399.2334 | 2504.8825 | 2342.0122 | NORMAL
298.8907 | 1 | 296.113 | 0.68163 | 2 | 73773.932 | 13399.2334 | 3162.948 | 2342.0122 | NORMAL
298.8907 | 1 | 296.113 | 0.68163 | 2 | 90321.356 | 13399.2334 | 3773.0104 | 2342.0122 | NORMAL
298.8907 | 1 | 296.113 | 0.68163 | 2 | 106868.78 | 13399.2334 | 4335.9766 | 2342.0122 | NORMAL
298.8907 | 1 | 296.113 | 0.84923 | 1 | 57226.508 | 8839.7893 | 1605.299 | 1506.1078 | NORMAL
298.8907 | 1 | 296.113 | 0.84923 | 1 | 73773.932 | 8839.7893 | 2014.1872 | 1506.1078 | NORMAL
298.8907 | 1 | 296.113 | 0.84923 | 1 | 90321.356 | 8839.7893 | 2390.5969 | 1506.1078 | NORMAL
298.8907 | 1 | 296.113 | 0.84923 | 1 | 106868.78 | 8839.7893 | 2736.6577 | 1506.1078 | NORMAL
298.8907 | 1 | 296.113 | 0.84923 | 2 | 57226.508 | 12944.4309 | 2385.0016 | 2327.7796 | NORMAL
298.8907 | 1 | 296.113 | 0.84923 | 2 | 73773.932 | 12944.4309 | 3001.9236 | 2327.7796 | NORMAL
298.8907 | 1 | 296.113 | 0.84923 | 2 | 90321.356 | 12944.4309 | 3571.8409 | 2327.7796 | NORMAL
298.8907 | 1 | 296.113 | 0.84923 | 2 | 106868.78 | 12944.4309 | 4096.8159 | 2327.7796 | NORMAL
298.8907 | 1 | 300.7426 | 0.34644 | 1 | 57226.508 | 12670.1259 | 1969.4418 | 1504.5713 | NORMAL
298.8907 | 1 | 300.7426 | 0.34644 | 1 | 73773.932 | 12670.1259 | 2550.7221 | 1504.5713 | NORMAL
298.8907 | 1 | 300.7426 | 0.34644 | 1 | 90321.356 | 12670.1259 | 3111.8969 | 1504.5713 | NORMAL
298.8907 | 1 | 300.7426 | 0.34644 | 1 | 106868.78 | 12670.1259 | 3648.2664 | 1504.5713 | NORMAL
298.8907 | 1 | 300.7426 | 0.34644 | 2 | 57226.508 | 17189.1466 | 2781.2012 | 2026.9067 | NORMAL
298.8907 | 1 | 300.7426 | 0.34644 | 2 | 73773.932 | 17189.1466 | 3644.564 | 2026.9067 | NORMAL
298.8907 | 1 | 300.7426 | 0.34644 | 2 | 90321.356 | 17189.1466 | 4491.369 | 2026.9067 | NORMAL
298.8907 | 1 | 300.7426 | 0.34644 | 2 | 106868.78 | 17189.1466 | 5308.314 | 2026.9067 | NORMAL
298.8907 | 1 | 300.7426 | 0.51403 | 1 | 57226.508 | 12150.9549 | 1821.7638 | 1549.9888 | NORMAL
298.8907 | 1 | 300.7426 | 0.51403 | 1 | 73773.932 | 12150.9549 | 2336.079 | 1549.9888 | NORMAL
298.8907 | 1 | 300.7426 | 0.51403 | 1 | 90321.356 | 12150.9549 | 2825.7606 | 1549.9888 | NORMAL
298.8907 | 1 | 300.7426 | 0.51403 | 1 | 106868.78 | 12150.9549 | 3289.4731 | 1549.9888 | NORMAL
298.8907 | 1 | 300.7426 | 0.51403 | 2 | 57226.508 | 17520.8585 | 2701.8962 | 2302.1317 | NORMAL
298.8907 | 1 | 300.7426 | 0.51403 | 2 | 73773.932 | 17520.8585 | 3491.5343 | 2302.1317 | NORMAL
298.8907 | 1 | 300.7426 | 0.51403 | 2 | 90321.356 | 17520.8585 | 4251.5028 | 2302.1317 | NORMAL
298.8907 | 1 | 300.7426 | 0.51403 | 2 | 106868.78 | 17520.8585 | 4976.4276 | 2302.1317 | NORMAL
298.8907 | 1 | 300.7426 | 0.68163 | 1 | 57226.508 | 11609.4308 | 1711.1235 | 1531.9123 | NORMAL
298.8907 | 1 | 300.7426 | 0.68163 | 1 | 73773.932 | 11609.4308 | 2184.3293 | 1531.9123 | NORMAL
298.8907 | 1 | 300.7426 | 0.68163 | 1 | 90321.356 | 11609.4308 | 2632.0207 | 1531.9123 | NORMAL
298.8907 | 1 | 300.7426 | 0.68163 | 1 | 106868.78 | 11609.4308 | 3054.0812 | 1531.9123 | NORMAL
298.8907 | 1 | 300.7426 | 0.68163 | 2 | 57226.508 | 16962.7628 | 2549.6727 | 2342.0122 | NORMAL
298.8907 | 1 | 300.7426 | 0.68163 | 2 | 73773.932 | 16962.7628 | 3271.7259 | 2342.0122 | NORMAL
298.8907 | 1 | 300.7426 | 0.68163 | 2 | 90321.356 | 16962.7628 | 3959.8561 | 2342.0122 | NORMAL
298.8907 | 1 | 300.7426 | 0.68163 | 2 | 106868.78 | 16962.7628 | 4611.9269 | 2342.0122 | NORMAL
298.8907 | 1 | 300.7426 | 0.84923 | 1 | 57226.508 | 11190.7333 | 1633.6444 | 1506.1078 | NORMAL
298.8907 | 1 | 300.7426 | 0.84923 | 1 | 73773.932 | 11190.7333 | 2080.2498 | 1506.1078 | NORMAL
298.8907 | 1 | 300.7426 | 0.84923 | 1 | 90321.356 | 11190.7333 | 2501.299 | 1506.1078 | NORMAL
298.8907 | 1 | 300.7426 | 0.84923 | 1 | 106868.78 | 11190.7333 | 2897.2494 | 1506.1078 | NORMAL
298.8907 | 1 | 300.7426 | 0.84923 | 2 | 57226.508 | 16387.0053 | 2427.3348 | 2327.7796 | NORMAL
298.8907 | 1 | 300.7426 | 0.84923 | 2 | 73773.932 | 16387.0053 | 3102.6417 | 2327.7796 | NORMAL
298.8907 | 1 | 300.7426 | 0.84923 | 2 | 90321.356 | 16387.0053 | 3742.7091 | 2327.7796 | NORMAL
298.8907 | 1 | 300.7426 | 0.84923 | 2 | 106868.78 | 16387.0053 | 4346.9172 | 2327.7796 | NORMAL
298.8907 | 1 | 305.3722 | 0.34644 | 1 | 57226.508 | 16404.1423 | 2045.3697 | 1504.5713 | NORMAL
298.8907 | 1 | 305.3722 | 0.34644 | 1 | 73773.932 | 16404.1423 | 2696.2962 | 1504.5713 | NORMAL
298.8907 | 1 | 305.3722 | 0.34644 | 1 | 90321.356 | 16404.1423 | 3344.2885 | 1504.5713 | NORMAL
298.8907 | 1 | 305.3722 | 0.34644 | 1 | 106868.78 | 16404.1423 | 3983.1966 | 1504.5713 | NORMAL
298.8907 | 1 | 305.3722 | 0.34644 | 2 | 57226.508 | 22254.9649 | 2891.8153 | 2026.9067 | NORMAL
298.8907 | 1 | 305.3722 | 0.34644 | 2 | 73773.932 | 22254.9649 | 3867.8712 | 2026.9067 | NORMAL
298.8907 | 1 | 305.3722 | 0.34644 | 2 | 90321.356 | 22254.9649 | 4863.2885 | 2026.9067 | NORMAL
298.8907 | 1 | 305.3722 | 0.34644 | 2 | 106868.78 | 22254.9649 | 5862.9223 | 2026.9067 | NORMAL
298.8907 | 1 | 305.3722 | 0.51403 | 1 | 57226.508 | 15731.9663 | 1890.5996 | 1549.9888 | NORMAL
298.8907 | 1 | 305.3722 | 0.51403 | 1 | 73773.932 | 15731.9663 | 2462.4878 | 1549.9888 | NORMAL
298.8907 | 1 | 305.3722 | 0.51403 | 1 | 90321.356 | 15731.9663 | 3020.5757 | 1549.9888 | NORMAL
298.8907 | 1 | 305.3722 | 0.51403 | 1 | 106868.78 | 15731.9663 | 3562.1544 | 1549.9888 | NORMAL
298.8907 | 1 | 305.3722 | 0.51403 | 2 | 57226.508 | 22684.4357 | 2805.5362 | 2302.1317 | NORMAL
298.8907 | 1 | 305.3722 | 0.51403 | 2 | 73773.932 | 22684.4357 | 3688.3109 | 2302.1317 | NORMAL
298.8907 | 1 | 305.3722 | 0.51403 | 2 | 90321.356 | 22684.4357 | 4563.1304 | 2302.1317 | NORMAL
298.8907 | 1 | 305.3722 | 0.51403 | 2 | 106868.78 | 22684.4357 | 5422.603 | 2302.1317 | NORMAL
298.8907 | 1 | 305.3722 | 0.68163 | 1 | 57226.508 | 15030.8495 | 1775.3326 | 1531.9123 | NORMAL
298.8907 | 1 | 305.3722 | 0.68163 | 1 | 73773.932 | 15030.8495 | 2299.992 | 1531.9123 | NORMAL
298.8907 | 1 | 305.3722 | 0.68163 | 1 | 90321.356 | 15030.8495 | 2807.5178 | 1531.9123 | NORMAL
298.8907 | 1 | 305.3722 | 0.68163 | 1 | 106868.78 | 15030.8495 | 3296.536 | 1531.9123 | NORMAL
298.8907 | 1 | 305.3722 | 0.68163 | 2 | 57226.508 | 21961.8634 | 2646.126 | 2342.0122 | NORMAL
298.8907 | 1 | 305.3722 | 0.68163 | 2 | 73773.932 | 21961.8634 | 3449.3717 | 2342.0122 | NORMAL
298.8907 | 1 | 305.3722 | 0.68163 | 2 | 90321.356 | 21961.8634 | 4234.2891 | 2342.0122 | NORMAL
298.8907 | 1 | 305.3722 | 0.68163 | 2 | 106868.78 | 21961.8634 | 4996.8157 | 2342.0122 | NORMAL
298.8907 | 1 | 305.3722 | 0.84923 | 1 | 57226.508 | 14488.7576 | 1694.7514 | 1506.1078 | NORMAL
298.8907 | 1 | 305.3722 | 0.84923 | 1 | 73773.932 | 14488.7576 | 2189.1718 | 1506.1078 | NORMAL
298.8907 | 1 | 305.3722 | 0.84923 | 1 | 90321.356 | 14488.7576 | 2665.1745 | 1506.1078 | NORMAL
298.8907 | 1 | 305.3722 | 0.84923 | 1 | 106868.78 | 14488.7576 | 3122.0452 | 1506.1078 | NORMAL
298.8907 | 1 | 305.3722 | 0.84923 | 2 | 57226.508 | 21216.4244 | 2518.5878 | 2327.7796 | NORMAL
298.8907 | 1 | 305.3722 | 0.84923 | 2 | 73773.932 | 21216.4244 | 3267.9331 | 2327.7796 | NORMAL
298.8907 | 1 | 305.3722 | 0.84923 | 2 | 90321.356 | 21216.4244 | 3994.6326 | 2327.7796 | NORMAL
298.8907 | 1 | 305.3722 | 0.84923 | 2 | 106868.78 | 21216.4244 | 4696.2649 | 2327.7796 | NORMAL
311.8537 | 0 | 291.4833 | 0.34644 | 1 | 57226.508 | 12006.2218 | 12702.3884 | 2033.4333 | NORMAL
311.8537 | 0 | 291.4833 | 0.34644 | 1 | 73773.932 | 10740.918 | 11519.9598 | 2033.4333 | NORMAL
311.8537 | 0 | 291.4833 | 0.34644 | 1 | 90321.356 | 9904.5582 | 10715.8189 | 2033.4333 | NORMAL
311.8537 | 0 | 291.4833 | 0.34644 | 1 | 106868.78 | 9316.7539 | 10131.8372 | 2033.4333 | NORMAL
311.8537 | 0 | 291.4833 | 0.34644 | 2 | 57226.508 | 16288.4496 | 16589.7673 | 2739.3714 | NORMAL
311.8537 | 0 | 291.4833 | 0.34644 | 2 | 73773.932 | 14571.8532 | 14958.9983 | 2739.3714 | NORMAL
311.8537 | 0 | 291.4833 | 0.34644 | 2 | 90321.356 | 13437.1911 | 13874.754 | 2739.3714 | NORMAL
311.8537 | 0 | 291.4833 | 0.34644 | 2 | 106868.78 | 12639.7363 | 13103.0783 | 2739.3714 | NORMAL
311.8537 | 0 | 291.4833 | 0.51403 | 1 | 57226.508 | 11514.255 | 13373.5124 | 2094.8152 | NORMAL
311.8537 | 0 | 291.4833 | 0.51403 | 1 | 73773.932 | 10300.7983 | 12186.3911 | 2094.8152 | NORMAL
311.8537 | 0 | 291.4833 | 0.51403 | 1 | 90321.356 | 9498.7091 | 11351.3232 | 2094.8152 | NORMAL
311.8537 | 0 | 291.4833 | 0.51403 | 1 | 106868.78 | 8934.9907 | 10728.2007 | 2094.8152 | NORMAL
311.8537 | 0 | 291.4833 | 0.51403 | 2 | 57226.508 | 16602.7801 | 17808.193 | 3111.3389 | NORMAL
311.8537 | 0 | 291.4833 | 0.51403 | 2 | 73773.932 | 14853.0572 | 16169.8378 | 3111.3389 | NORMAL
311.8537 | 0 | 291.4833 | 0.51403 | 2 | 90321.356 | 13696.4987 | 15048.3729 | 3111.3389 | NORMAL
311.8537 | 0 | 291.4833 | 0.51403 | 2 | 106868.78 | 12883.6548 | 14229.5816 | 3111.3389 | NORMAL
311.8537 | 0 | 291.4833 | 0.68163 | 1 | 57226.508 | 11001.1063 | 13920.159 | 2070.3847 | NORMAL
311.8537 | 0 | 291.4833 | 0.68163 | 1 | 73773.932 | 9841.7289 | 12697.7063 | 2070.3847 | NORMAL
311.8537 | 0 | 291.4833 | 0.68163 | 1 | 90321.356 | 9075.386 | 11821.9072 | 2070.3847 | NORMAL
311.8537 | 0 | 291.4833 | 0.68163 | 1 | 106868.78 | 8536.7905 | 11158.8335 | 2070.3847 | NORMAL
311.8537 | 0 | 291.4833 | 0.68163 | 2 | 57226.508 | 16073.9281 | 18487.0784 | 3165.2376 | NORMAL
311.8537 | 0 | 291.4833 | 0.68163 | 2 | 73773.932 | 14379.9396 | 16841.8942 | 3165.2376 | NORMAL
311.8537 | 0 | 291.4833 | 0.68163 | 2 | 90321.356 | 13260.2211 | 15687.6909 | 3165.2376 | NORMAL
311.8537 | 0 | 291.4833 | 0.68163 | 2 | 106868.78 | 12473.2689 | 14828.2484 | 3165.2376 | NORMAL
311.8537 | 0 | 291.4833 | 0.84923 | 1 | 57226.508 | 10604.3482 | 14368.4812 | 2035.5099 | NORMAL
311.8537 | 0 | 291.4833 | 0.84923 | 1 | 73773.932 | 9486.7842 | 13106.7392 | 2035.5099 | NORMAL
311.8537 | 0 | 291.4833 | 0.84923 | 1 | 90321.356 | 8748.0796 | 12193.4311 | 2035.5099 | NORMAL
311.8537 | 0 | 291.4833 | 0.84923 | 1 | 106868.78 | 8228.9087 | 11496.2142 | 2035.5099 | NORMAL
311.8537 | 0 | 291.4833 | 0.84923 | 2 | 57226.508 | 15528.3399 | 19086.2599 | 3146.0021 | NORMAL
311.8537 | 0 | 291.4833 | 0.84923 | 2 | 73773.932 | 13891.8495 | 17406.9929 | 3146.0021 | NORMAL
311.8537 | 0 | 291.4833 | 0.84923 | 2 | 90321.356 | 12810.137 | 16210.3609 | 3146.0021 | NORMAL
311.8537 | 0 | 291.4833 | 0.84923 | 2 | 106868.78 | 12049.8958 | 15308.2482 | 3146.0021 | NORMAL
311.8537 | 0 | 296.113 | 0.34644 | 1 | 57226.508 | 10729.8863 | 12060.0616 | 2033.4333 | NORMAL
311.8537 | 0 | 296.113 | 0.34644 | 1 | 73773.932 | 9582.2985 | 10994.1072 | 2033.4333 | NORMAL
311.8537 | 0 | 296.113 | 0.34644 | 1 | 90321.356 | 8850.4559 | 10269.999 | 2033.4333 | NORMAL
311.8537 | 0 | 296.113 | 0.34644 | 1 | 106868.78 | 8356.895 | 9747.1074 | 2033.4333 | NORMAL
311.8537 | 0 | 296.113 | 0.34644 | 2 | 57226.508 | 14556.8868 | 15281.1585 | 2739.3714 | NORMAL
311.8537 | 0 | 296.113 | 0.34644 | 2 | 73773.932 | 12999.9918 | 13850.407 | 2739.3714 | NORMAL
311.8537 | 0 | 296.113 | 0.34644 | 2 | 90321.356 | 12007.125 | 12911.6455 | 2739.3714 | NORMAL
311.8537 | 0 | 296.113 | 0.34644 | 2 | 106868.78 | 11337.5269 | 12253.756 | 2739.3714 | NORMAL
311.8537 | 0 | 296.113 | 0.51403 | 1 | 57226.508 | 10290.2186 | 13235.5267 | 2094.8152 | NORMAL
311.8537 | 0 | 296.113 | 0.51403 | 1 | 73773.932 | 9189.6543 | 12107.2751 | 2094.8152 | NORMAL
311.8537 | 0 | 296.113 | 0.51403 | 1 | 90321.356 | 8487.7998 | 11310.3018 | 2094.8152 | NORMAL
311.8537 | 0 | 296.113 | 0.51403 | 1 | 106868.78 | 8014.463 | 10715.6515 | 2094.8152 | NORMAL
311.8537 | 0 | 296.113 | 0.51403 | 2 | 57226.508 | 14837.8021 | 17042.8633 | 3111.3389 | NORMAL
311.8537 | 0 | 296.113 | 0.51403 | 2 | 73773.932 | 13250.8625 | 15551.6935 | 3111.3389 | NORMAL
311.8537 | 0 | 296.113 | 0.51403 | 2 | 90321.356 | 12238.8355 | 14530.3958 | 3111.3389 | NORMAL
311.8537 | 0 | 296.113 | 0.51403 | 2 | 106868.78 | 11556.3157 | 13787.8119 | 3111.3389 | NORMAL
311.8537 | 0 | 296.113 | 0.68163 | 1 | 57226.508 | 9831.6208 | 14113.5632 | 2070.3847 | NORMAL
311.8537 | 0 | 296.113 | 0.68163 | 1 | 73773.932 | 8780.1046 | 12916.2256 | 2070.3847 | NORMAL
311.8537 | 0 | 296.113 | 0.68163 | 1 | 90321.356 | 8109.5292 | 12054.217 | 2070.3847 | NORMAL
311.8537 | 0 | 296.113 | 0.68163 | 1 | 106868.78 | 7657.2873 | 11400.5982 | 2070.3847 | NORMAL
311.8537 | 0 | 296.113 | 0.68163 | 2 | 57226.508 | 14365.1703 | 18234.8463 | 3165.2376 | NORMAL
311.8537 | 0 | 296.113 | 0.68163 | 2 | 73773.932 | 12828.7799 | 16678.0508 | 3165.2376 | NORMAL
311.8537 | 0 | 296.113 | 0.68163 | 2 | 90321.356 | 11848.9892 | 15581.4943 | 3165.2376 | NORMAL
311.8537 | 0 | 296.113 | 0.68163 | 2 | 106868.78 | 11188.2099 | 14765.2723 | 3165.2376 | NORMAL
311.8537 | 0 | 296.113 | 0.84923 | 1 | 57226.508 | 9477.0405 | 14785.4534 | 2035.5099 | NORMAL
311.8537 | 0 | 296.113 | 0.84923 | 1 | 73773.932 | 8463.4476 | 13528.6326 | 2035.5099 | NORMAL
311.8537 | 0 | 296.113 | 0.84923 | 1 | 90321.356 | 7817.0567 | 12614.2831 | 2035.5099 | NORMAL
311.8537 | 0 | 296.113 | 0.84923 | 1 | 106868.78 | 7381.1251 | 11914.717 | 2035.5099 | NORMAL
311.8537 | 0 | 296.113 | 0.84923 | 2 | 57226.508 | 13877.5815 | 19210.1308 | 3146.0021 | NORMAL
311.8537 | 0 | 296.113 | 0.84923 | 2 | 73773.932 | 12393.3399 | 17579.8409 | 3146.0021 | NORMAL
311.8537 | 0 | 296.113 | 0.84923 | 2 | 90321.356 | 11446.8057 | 16412.575 | 3146.0021 | NORMAL
311.8537 | 0 | 296.113 | 0.84923 | 2 | 106868.78 | 10808.4548 | 15531.6349 | 3146.0021 | NORMAL
311.8537 | 0 | 300.7426 | 0.34644 | 1 | 57226.508 | 9716.1741 | 11878.0793 | 2033.4333 | NORMAL
311.8537 | 0 | 300.7426 | 0.34644 | 1 | 73773.932 | 8705.1344 | 10908.8814 | 2033.4333 | NORMAL
311.8537 | 0 | 300.7426 | 0.34644 | 1 | 90321.356 | 8095.0448 | 10251.9038 | 2033.4333 | NORMAL
311.8537 | 0 | 300.7426 | 0.34644 | 1 | 106868.78 | 7711.8555 | 9782.0004 | 2033.4333 | NORMAL
311.8537 | 0 | 300.7426 | 0.34644 | 2 | 57226.508 | 13181.6165 | 14575.7336 | 2739.3714 | NORMAL
311.8537 | 0 | 300.7426 | 0.34644 | 2 | 73773.932 | 11809.972 | 13332.0811 | 2739.3714 | NORMAL
311.8537 | 0 | 300.7426 | 0.34644 | 2 | 90321.356 | 10982.2833 | 12525.1524 | 2739.3714 | NORMAL
311.8537 | 0 | 300.7426 | 0.34644 | 2 | 106868.78 | 10462.4229 | 11970.7604 | 2739.3714 | NORMAL
311.8537 | 0 | 300.7426 | 0.51403 | 1 | 57226.508 | 9318.0442 | 13518.5044 | 2094.8152 | NORMAL
311.8537 | 0 | 300.7426 | 0.51403 | 1 | 73773.932 | 8348.4329 | 12435.7627 | 2094.8152 | NORMAL
311.8537 | 0 | 300.7426 | 0.51403 | 1 | 90321.356 | 7763.3423 | 11669.818 | 2094.8152 | NORMAL
311.8537 | 0 | 300.7426 | 0.51403 | 1 | 106868.78 | 7395.8546 | 11096.5268 | 2094.8152 | NORMAL
311.8537 | 0 | 300.7426 | 0.51403 | 2 | 57226.508 | 13435.9921 | 16911.046 | 3111.3389 | NORMAL
311.8537 | 0 | 300.7426 | 0.51403 | 2 | 73773.932 | 12037.8779 | 15539.8832 | 3111.3389 | NORMAL
311.8537 | 0 | 300.7426 | 0.51403 | 2 | 90321.356 | 11194.2167 | 14601.7409 | 3111.3389 | NORMAL
311.8537 | 0 | 300.7426 | 0.51403 | 2 | 106868.78 | 10664.3241 | 13925.014 | 3111.3389 | NORMAL
311.8537 | 0 | 300.7426 | 0.68163 | 1 | 57226.508 | 8902.7727 | 14695.563 | 2070.3847 | NORMAL
311.8537 | 0 | 300.7426 | 0.68163 | 1 | 73773.932 | 7976.3735 | 13516.4973 | 2070.3847 | NORMAL
311.8537 | 0 | 300.7426 | 0.68163 | 1 | 90321.356 | 7417.3582 | 12649.3175 | 2070.3847 | NORMAL
311.8537 | 0 | 300.7426 | 0.68163 | 1 | 106868.78 | 7066.2481 | 11967.8703 | 2070.3847 | NORMAL
311.8537 | 0 | 300.7426 | 0.68163 | 2 | 57226.508 | 13008.0125 | 18573.2483 | 3165.2376 | NORMAL
311.8537 | 0 | 300.7426 | 0.68163 | 2 | 73773.932 | 11654.4328 | 17085.1016 | 3165.2376 | NORMAL
311.8537 | 0 | 300.7426 | 0.68163 | 2 | 90321.356 | 10837.6449 | 16035.5268 | 3165.2376 | NORMAL
311.8537 | 0 | 300.7426 | 0.68163 | 2 | 106868.78 | 10324.6311 | 15257.1238 | 3165.2376 | NORMAL
311.8537 | 0 | 300.7426 | 0.84923 | 1 | 57226.508 | 8581.6916 | 15571.1816 | 2035.5099 | NORMAL
311.8537 | 0 | 300.7426 | 0.84923 | 1 | 73773.932 | 7688.7033 | 14316.3733 | 2035.5099 | NORMAL
311.8537 | 0 | 300.7426 | 0.84923 | 1 | 90321.356 | 7149.8491 | 13349.7063 | 2035.5099 | NORMAL
311.8537 | 0 | 300.7426 | 0.84923 | 1 | 106868.78 | 6811.4018 | 12608.3409 | 2035.5099 | NORMAL
311.8537 | 0 | 300.7426 | 0.84923 | 2 | 57226.508 | 12566.4889 | 19887.871 | 3146.0021 | NORMAL
311.8537 | 0 | 300.7426 | 0.84923 | 2 | 73773.932 | 11258.853 | 18294.2675 | 3146.0021 | NORMAL
311.8537 | 0 | 300.7426 | 0.84923 | 2 | 90321.356 | 10469.7889 | 17148.8663 | 3146.0021 | NORMAL
311.8537 | 0 | 300.7426 | 0.84923 | 2 | 106868.78 | 9974.188 | 16238.4831 | 3146.0021 | NORMAL
311.8537 | 0 | 305.3722 | 0.34644 | 1 | 57226.508 | 8921.0527 | 12051.017 | 2033.4333 | NORMAL
311.8537 | 0 | 305.3722 | 0.34644 | 1 | 73773.932 | 8061.8436 | 11157.8517 | 2033.4333 | NORMAL
311.8537 | 0 | 305.3722 | 0.34644 | 1 | 90321.356 | 7587.3184 | 10555.2726 | 2033.4333 | NORMAL
311.8537 | 0 | 305.3722 | 0.34644 | 1 | 106868.78 | 7327.1447 | 10130.1162 | 2033.4333 | NORMAL
311.8537 | 0 | 305.3722 | 0.34644 | 2 | 57226.508 | 12102.9012 | 14375.1681 | 2739.3714 | NORMAL
311.8537 | 0 | 305.3722 | 0.34644 | 2 | 73773.932 | 10937.2403 | 13286.1354 | 2739.3714 | NORMAL
311.8537 | 0 | 305.3722 | 0.34644 | 2 | 90321.356 | 10293.4674 | 12588.505 | 2739.3714 | NORMAL
311.8537 | 0 | 305.3722 | 0.34644 | 2 | 106868.78 | 9940.4982 | 12122.1324 | 2739.3714 | NORMAL
311.8537 | 0 | 305.3722 | 0.51403 | 1 | 57226.508 | 8555.5037 | 14115.9834 | 2094.8152 | NORMAL
311.8537 | 0 | 305.3722 | 0.51403 | 1 | 73773.932 | 7731.5016 | 13067.6824 | 2094.8152 | NORMAL
311.8537 | 0 | 305.3722 | 0.51403 | 1 | 90321.356 | 7276.4205 | 12279.7914 | 2094.8152 | NORMAL
311.8537 | 0 | 305.3722 | 0.51403 | 1 | 106868.78 | 7026.9077 | 11699.6123 | 2094.8152 | NORMAL
311.8537 | 0 | 305.3722 | 0.51403 | 2 | 57226.508 | 12336.46 | 17262.1963 | 3111.3389 | NORMAL
311.8537 | 0 | 305.3722 | 0.51403 | 2 | 73773.932 | 11148.3045 | 15984.8761 | 3111.3389 | NORMAL
311.8537 | 0 | 305.3722 | 0.51403 | 2 | 90321.356 | 10492.1082 | 15114.1075 | 3111.3389 | NORMAL
311.8537 | 0 | 305.3722 | 0.51403 | 2 | 106868.78 | 10132.3275 | 14477.9042 | 3111.3389 | NORMAL
311.8537 | 0 | 305.3722 | 0.68163 | 1 | 57226.508 | 8174.2158 | 15568.9062 | 2070.3847 | NORMAL
311.8537 | 0 | 305.3722 | 0.68163 | 1 | 73773.932 | 7386.9365 | 14350.7852 | 2070.3847 | NORMAL
311.8537 | 0 | 305.3722 | 0.68163 | 1 | 90321.356 | 6952.1367 | 13453.2502 | 2070.3847 | NORMAL
311.8537 | 0 | 305.3722 | 0.68163 | 1 | 106868.78 | 6713.7438 | 12778.7483 | 2070.3847 | NORMAL
311.8537 | 0 | 305.3722 | 0.68163 | 2 | 57226.508 | 11943.5041 | 19353.1324 | 3165.2376 | NORMAL
311.8537 | 0 | 305.3722 | 0.68163 | 2 | 73773.932 | 10793.1951 | 17918.2125 | 3165.2376 | NORMAL
311.8537 | 0 | 305.3722 | 0.68163 | 2 | 90321.356 | 10157.9008 | 16850.2583 | 3165.2376 | NORMAL
311.8537 | 0 | 305.3722 | 0.68163 | 2 | 106868.78 | 9809.5803 | 16060.8194 | 3165.2376 | NORMAL
311.8537 | 0 | 305.3722 | 0.84923 | 1 | 57226.508 | 7879.4104 | 16634.1251 | 2035.5099 | NORMAL
311.8537 | 0 | 305.3722 | 0.84923 | 1 | 73773.932 | 7120.5245 | 15288.6059 | 2035.5099 | NORMAL
311.8537 | 0 | 305.3722 | 0.84923 | 1 | 90321.356 | 6701.4059 | 14310.18 | 2035.5099 | NORMAL
311.8537 | 0 | 305.3722 | 0.84923 | 1 | 106868.78 | 6471.6107 | 13566.695 | 2035.5099 | NORMAL
311.8537 | 0 | 305.3722 | 0.84923 | 2 | 57226.508 | 11538.1125 | 20979.9336 | 3146.0021 | NORMAL
311.8537 | 0 | 305.3722 | 0.84923 | 2 | 73773.932 | 10426.8478 | 19365.0763 | 3146.0021 | NORMAL
311.8537 | 0 | 305.3722 | 0.84923 | 2 | 90321.356 | 9813.1169 | 18167.4602 | 3146.0021 | NORMAL
311.8537 | 0 | 305.3722 | 0.84923 | 2 | 106868.78 | 9476.6193 | 17272.6933 | 3146.0021 | NORMAL
311.8537 | 0.33333 | 291.4833 | 0.34644 | 1 | 57226.508 | 8230.8951 | 6496.1162 | 2033.4333 | NORMAL
311.8537 | 0.33333 | 291.4833 | 0.34644 | 1 | 73773.932 | 7954.0492 | 6551.4004 | 2033.4333 | NORMAL
311.8537 | 0.33333 | 291.4833 | 0.34644 | 1 | 90321.356 | 7757.9272 | 6584.6681 | 2033.4333 | NORMAL
311.8537 | 0.33333 | 291.4833 | 0.34644 | 1 | 106868.78 | 7614.62 | 6607.4613 | 2033.4333 | NORMAL
311.8537 | 0.33333 | 291.4833 | 0.34644 | 2 | 57226.508 | 11166.587 | 8114.6016 | 2739.3714 | NORMAL
311.8537 | 0.33333 | 291.4833 | 0.34644 | 2 | 73773.932 | 10790.9992 | 8298.9878 | 2739.3714 | NORMAL
311.8537 | 0.33333 | 291.4833 | 0.34644 | 2 | 90321.356 | 10524.9268 | 8423.8153 | 2739.3714 | NORMAL
311.8537 | 0.33333 | 291.4833 | 0.34644 | 2 | 106868.78 | 10330.5066 | 8515.5053 | 2739.3714 | NORMAL
311.8537 | 0.33333 | 291.4833 | 0.51403 | 1 | 57226.508 | 7893.626 | 7200.3734 | 2094.8152 | NORMAL
311.8537 | 0.33333 | 291.4833 | 0.51403 | 1 | 73773.932 | 7628.1242 | 7136.5594 | 2094.8152 | NORMAL
311.8537 | 0.33333 | 291.4833 | 0.51403 | 1 | 90321.356 | 7440.0384 | 7077.5668 | 2094.8152 | NORMAL
311.8537 | 0.33333 | 291.4833 | 0.51403 | 1 | 106868.78 | 7302.6034 | 7026.5074 | 2094.8152 | NORMAL
311.8537 | 0.33333 | 291.4833 | 0.51403 | 2 | 57226.508 | 11382.077 | 9207.5872 | 3111.3389 | NORMAL
311.8537 | 0.33333 | 291.4833 | 0.51403 | 2 | 73773.932 | 10999.2412 | 9254.6486 | 3111.3389 | NORMAL
311.8537 | 0.33333 | 291.4833 | 0.51403 | 2 | 90321.356 | 10728.0342 | 9278.3149 | 3111.3389 | NORMAL
311.8537 | 0.33333 | 291.4833 | 0.51403 | 2 | 106868.78 | 10529.8622 | 9292.1909 | 3111.3389 | NORMAL
311.8537 | 0.33333 | 291.4833 | 0.68163 | 1 | 57226.508 | 7541.8357 | 7656.3247 | 2070.3847 | NORMAL
311.8537 | 0.33333 | 291.4833 | 0.68163 | 1 | 73773.932 | 7288.1663 | 7510.8465 | 2070.3847 | NORMAL
311.8537 | 0.33333 | 291.4833 | 0.68163 | 1 | 90321.356 | 7108.4628 | 7388.0226 | 2070.3847 | NORMAL
311.8537 | 0.33333 | 291.4833 | 0.68163 | 1 | 106868.78 | 6977.1528 | 7285.2139 | 2070.3847 | NORMAL
311.8537 | 0.33333 | 291.4833 | 0.68163 | 2 | 57226.508 | 11019.5212 | 9921.66 | 3165.2376 | NORMAL
311.8537 | 0.33333 | 291.4833 | 0.68163 | 2 | 73773.932 | 10648.88 | 9847.4326 | 3165.2376 | NORMAL
311.8537 | 0.33333 | 291.4833 | 0.68163 | 2 | 90321.356 | 10386.3118 | 9776.6626 | 3165.2376 | NORMAL
311.8537 | 0.33333 | 291.4833 | 0.68163 | 2 | 106868.78 | 10194.4522 | 9714.7328 | 3165.2376 | NORMAL
311.8537 | 0.33333 | 291.4833 | 0.84923 | 1 | 57226.508 | 7269.8372 | 7995.2928 | 2035.5099 | NORMAL
311.8537 | 0.33333 | 291.4833 | 0.84923 | 1 | 73773.932 | 7025.3164 | 7791.6925 | 2035.5099 | NORMAL
311.8537 | 0.33333 | 291.4833 | 0.84923 | 1 | 90321.356 | 6852.0941 | 7623.0158 | 2035.5099 | NORMAL
311.8537 | 0.33333 | 291.4833 | 0.84923 | 1 | 106868.78 | 6725.5198 | 7482.7357 | 2035.5099 | NORMAL
311.8537 | 0.33333 | 291.4833 | 0.84923 | 2 | 57226.508 | 10645.4919 | 10433.3253 | 3146.0021 | NORMAL
311.8537 | 0.33333 | 291.4833 | 0.84923 | 2 | 73773.932 | 10287.4311 | 10267.6549 | 3146.0021 | NORMAL
311.8537 | 0.33333 | 291.4833 | 0.84923 | 2 | 90321.356 | 10033.7751 | 10125.6201 | 3146.0021 | NORMAL
311.8537 | 0.33333 | 291.4833 | 0.84923 | 2 | 106868.78 | 9848.4277 | 10006.0634 | 3146.0021 | NORMAL
311.8537 | 0.33333 | 296.113 | 0.34644 | 1 | 57226.508 | 7397.2786 | 6124.3812 | 2033.4333 | NORMAL
311.8537 | 0.33333 | 296.113 | 0.34644 | 1 | 73773.932 | 7274.7507 | 6189.1744 | 2033.4333 | NORMAL
311.8537 | 0.33333 | 296.113 | 0.34644 | 1 | 90321.356 | 7202.899 | 6248.9222 | 2033.4333 | NORMAL
311.8537 | 0.33333 | 296.113 | 0.34644 | 1 | 106868.78 | 7163.389 | 6306.0703 | 2033.4333 | NORMAL
311.8537 | 0.33333 | 296.113 | 0.34644 | 2 | 57226.508 | 10035.6467 | 7422.0115 | 2739.3714 | NORMAL
311.8537 | 0.33333 | 296.113 | 0.34644 | 2 | 73773.932 | 9869.417 | 7626.0033 | 2739.3714 | NORMAL
311.8537 | 0.33333 | 296.113 | 0.34644 | 2 | 90321.356 | 9771.9382 | 7794.5471 | 2739.3714 | NORMAL
311.8537 | 0.33333 | 296.113 | 0.34644 | 2 | 106868.78 | 9718.3363 | 7939.4018 | 2739.3714 | NORMAL
311.8537 | 0.33333 | 296.113 | 0.51403 | 1 | 57226.508 | 7094.1678 | 7004.8718 | 2094.8152 | NORMAL
311.8537 | 0.33333 | 296.113 | 0.51403 | 1 | 73773.932 | 6976.6606 | 6947.3633 | 2094.8152 | NORMAL
311.8537 | 0.33333 | 296.113 | 0.51403 | 1 | 90321.356 | 6907.7531 | 6907.9168 | 2094.8152 | NORMAL
311.8537 | 0.33333 | 296.113 | 0.51403 | 1 | 106868.78 | 6869.8621 | 6882.4007 | 2094.8152 | NORMAL
311.8537 | 0.33333 | 296.113 | 0.51403 | 2 | 57226.508 | 10229.3121 | 8734.6857 | 3111.3389 | NORMAL
311.8537 | 0.33333 | 296.113 | 0.51403 | 2 | 73773.932 | 10059.8746 | 8793.8386 | 3111.3389 | NORMAL
311.8537 | 0.33333 | 296.113 | 0.51403 | 2 | 90321.356 | 9960.5147 | 8851.9893 | 3111.3389 | NORMAL
311.8537 | 0.33333 | 296.113 | 0.51403 | 2 | 106868.78 | 9905.8784 | 8910.8345 | 3111.3389 | NORMAL
311.8537 | 0.33333 | 296.113 | 0.68163 | 1 | 57226.508 | 6778.0064 | 7607.8463 | 2070.3847 | NORMAL
311.8537 | 0.33333 | 296.113 | 0.68163 | 1 | 73773.932 | 6665.736 | 7466.3679 | 2070.3847 | NORMAL
311.8537 | 0.33333 | 296.113 | 0.68163 | 1 | 90321.356 | 6599.8995 | 7358.2258 | 2070.3847 | NORMAL
311.8537 | 0.33333 | 296.113 | 0.68163 | 1 | 106868.78 | 6563.6972 | 7274.8938 | 2070.3847 | NORMAL
311.8537 | 0.33333 | 296.113 | 0.68163 | 2 | 57226.508 | 9903.4756 | 9623.4385 | 3165.2376 | NORMAL
311.8537 | 0.33333 | 296.113 | 0.68163 | 2 | 73773.932 | 9739.4352 | 9558.4733 | 3165.2376 | NORMAL
311.8537 | 0.33333 | 296.113 | 0.68163 | 2 | 90321.356 | 9643.2402 | 9515.8504 | 3165.2376 | NORMAL
311.8537 | 0.33333 | 296.113 | 0.68163 | 2 | 106868.78 | 9590.3443 | 9490.6177 | 3165.2376 | NORMAL
311.8537 | 0.33333 | 296.113 | 0.84923 | 1 | 57226.508 | 6533.5557 | 8047.7392 | 2035.5099 | NORMAL
311.8537 | 0.33333 | 296.113 | 0.84923 | 1 | 73773.932 | 6425.3344 | 7846.8897 | 2035.5099 | NORMAL
311.8537 | 0.33333 | 296.113 | 0.84923 | 1 | 90321.356 | 6361.8723 | 7690.053 | 2035.5099 | NORMAL
311.8537 | 0.33333 | 296.113 | 0.84923 | 1 | 106868.78 | 6326.9755 | 7565.6143 | 2035.5099 | NORMAL
311.8537 | 0.33333 | 296.113 | 0.84923 | 2 | 57226.508 | 9567.3276 | 10301.2748 | 3146.0021 | NORMAL
311.8537 | 0.33333 | 296.113 | 0.84923 | 2 | 73773.932 | 9408.8551 | 10142.0721 | 3146.0021 | NORMAL
311.8537 | 0.33333 | 296.113 | 0.84923 | 2 | 90321.356 | 9315.9252 | 10022.4312 | 3146.0021 | NORMAL
311.8537 | 0.33333 | 296.113 | 0.84923 | 2 | 106868.78 | 9264.8246 | 9932.4548 | 3146.0021 | NORMAL
311.8537 | 0.33333 | 300.7426 | 0.34644 | 1 | 57226.508 | 7142.5876 | 6069.8937 | 2030.8213 | NORMAL
311.8537 | 0.33333 | 300.7426 | 0.34644 | 1 | 73773.932 | 7170.8765 | 6155.101 | 2030.9059 | NORMAL
311.8537 | 0.33333 | 300.7426 | 0.34644 | 1 | 90321.356 | 7224.0632 | 6249.909 | 2032.4813 | NORMAL
311.8537 | 0.33333 | 300.7426 | 0.34644 | 1 | 106868.78 | 7291.5762 | 6349.6738 | 2034.7288 | NORMAL
311.8537 | 0.33333 | 300.7426 | 0.34644 | 2 | 57226.508 | 9690.1156 | 7175.6217 | 2735.8526 | NORMAL
311.8537 | 0.33333 | 300.7426 | 0.34644 | 2 | 73773.932 | 9728.4943 | 7410.9014 | 2735.9666 | NORMAL
311.8537 | 0.33333 | 300.7426 | 0.34644 | 2 | 90321.356 | 9800.651 | 7640.5412 | 2738.0888 | NORMAL
311.8537 | 0.33333 | 300.7426 | 0.34644 | 2 | 106868.78 | 9892.2436 | 7862.5237 | 2741.1166 | NORMAL
311.8537 | 0.33333 | 300.7426 | 0.51403 | 1 | 57226.508 | 6849.913 | 7124.8758 | 2092.1243 | NORMAL
311.8537 | 0.33333 | 300.7426 | 0.51403 | 1 | 73773.932 | 6877.0427 | 7085.5193 | 2092.2115 | NORMAL
311.8537 | 0.33333 | 300.7426 | 0.51403 | 1 | 90321.356 | 6928.0501 | 7074.7942 | 2093.8344 | NORMAL
311.8537 | 0.33333 | 300.7426 | 0.51403 | 1 | 106868.78 | 6992.7966 | 7083.1602 | 2096.1497 | NORMAL
311.8537 | 0.33333 | 300.7426 | 0.51403 | 2 | 57226.508 | 9877.1131 | 8703.6226 | 3107.3423 | NORMAL
311.8537 | 0.33333 | 300.7426 | 0.51403 | 2 | 73773.932 | 9916.2324 | 8790.4642 | 3107.4718 | NORMAL
311.8537 | 0.33333 | 300.7426 | 0.51403 | 2 | 90321.356 | 9989.7815 | 8895.4753 | 3109.8822 | NORMAL
311.8537 | 0.33333 | 300.7426 | 0.51403 | 2 | 106868.78 | 10083.1417 | 9011.0076 | 3113.3211 | NORMAL
311.8537 | 0.33333 | 300.7426 | 0.68163 | 1 | 57226.508 | 6544.6371 | 7845.5028 | 2067.7252 | NORMAL
311.8537 | 0.33333 | 300.7426 | 0.68163 | 1 | 73773.932 | 6570.5578 | 7720.9393 | 2067.8114 | NORMAL
311.8537 | 0.33333 | 300.7426 | 0.68163 | 1 | 90321.356 | 6619.2919 | 7638.0864 | 2069.4154 | NORMAL
311.8537 | 0.33333 | 300.7426 | 0.68163 | 1 | 106868.78 | 6681.153 | 7583.8623 | 2071.7037 | NORMAL
311.8537 | 0.33333 | 300.7426 | 0.68163 | 2 | 57226.508 | 9562.4952 | 9769.1013 | 3161.1717 | NORMAL
311.8537 | 0.33333 | 300.7426 | 0.68163 | 2 | 73773.932 | 9600.3685 | 9729.5858 | 3161.3035 | NORMAL
311.8537 | 0.33333 | 300.7426 | 0.68163 | 2 | 90321.356 | 9671.5748 | 9727.5236 | 3163.7556 | NORMAL
311.8537 | 0.33333 | 300.7426 | 0.68163 | 2 | 106868.78 | 9761.9612 | 9750.2796 | 3167.2541 | NORMAL
311.8537 | 0.33333 | 300.7426 | 0.84923 | 1 | 57226.508 | 6308.6029 | 8368.0805 | 2032.8952 | NORMAL
311.8537 | 0.33333 | 300.7426 | 0.84923 | 1 | 73773.932 | 6333.5888 | 8183.3576 | 2032.98 | NORMAL
311.8537 | 0.33333 | 300.7426 | 0.84923 | 1 | 90321.356 | 6380.5653 | 8049.6717 | 2034.5569 | NORMAL
311.8537 | 0.33333 | 300.7426 | 0.84923 | 1 | 106868.78 | 6440.1953 | 7951.3648 | 2036.8067 | NORMAL
311.8537 | 0.33333 | 300.7426 | 0.84923 | 2 | 57226.508 | 9237.9209 | 10579.2857 | 3141.9609 | NORMAL
311.8537 | 0.33333 | 300.7426 | 0.84923 | 2 | 73773.932 | 9274.5086 | 10444.1162 | 3142.0919 | NORMAL
311.8537 | 0.33333 | 300.7426 | 0.84923 | 2 | 90321.356 | 9343.2981 | 10361.068 | 3144.5291 | NORMAL
311.8537 | 0.33333 | 300.7426 | 0.84923 | 2 | 106868.78 | 9430.6165 | 10313.5583 | 3148.0064 | NORMAL
311.8537 | 0.33333 | 305.3722 | 0.34644 | 1 | 57226.508 | 7479.8943 | 6250.2021 | 2040.3466 | NORMAL
311.8537 | 0.33333 | 305.3722 | 0.34644 | 1 | 73773.932 | 7648.4535 | 6366.7516 | 2043.891 | NORMAL
311.8537 | 0.33333 | 305.3722 | 0.34644 | 1 | 90321.356 | 7821.1609 | 6505.5991 | 2045.8398 | NORMAL
311.8537 | 0.33333 | 305.3722 | 0.34644 | 1 | 106868.78 | 7993.2266 | 6656.7152 | 2046.0085 | NORMAL
311.8537 | 0.33333 | 305.3722 | 0.34644 | 2 | 57226.508 | 10147.7287 | 7277.9493 | 2748.6848 | NORMAL
311.8537 | 0.33333 | 305.3722 | 0.34644 | 2 | 73773.932 | 10376.4074 | 7559.0008 | 2753.4597 | NORMAL
311.8537 | 0.33333 | 305.3722 | 0.34644 | 2 | 90321.356 | 10610.7139 | 7856.1873 | 2756.085 | NORMAL
311.8537 | 0.33333 | 305.3722 | 0.34644 | 2 | 106868.78 | 10844.1499 | 8158.8926 | 2756.3123 | NORMAL
311.8537 | 0.33333 | 305.3722 | 0.51403 | 1 | 57226.508 | 7173.3982 | 7452.1731 | 2101.9372 | NORMAL
311.8537 | 0.33333 | 305.3722 | 0.51403 | 1 | 73773.932 | 7335.0506 | 7441.3832 | 2105.5886 | NORMAL
311.8537 | 0.33333 | 305.3722 | 0.51403 | 1 | 90321.356 | 7500.6811 | 7468.6867 | 2107.5962 | NORMAL
311.8537 | 0.33333 | 305.3722 | 0.51403 | 1 | 106868.78 | 7665.6963 | 7520.0039 | 2107.77 | NORMAL
311.8537 | 0.33333 | 305.3722 | 0.51403 | 2 | 57226.508 | 10343.557 | 8991.3976 | 3121.9169 | NORMAL
311.8537 | 0.33333 | 305.3722 | 0.51403 | 2 | 73773.932 | 10576.6488 | 9121.0369 | 3127.3402 | NORMAL
311.8537 | 0.33333 | 305.3722 | 0.51403 | 2 | 90321.356 | 10815.4768 | 9285.5314 | 3130.322 | NORMAL
311.8537 | 0.33333 | 305.3722 | 0.51403 | 2 | 106868.78 | 11053.4176 | 9470.0053 | 3130.5802 | NORMAL
311.8537 | 0.33333 | 305.3722 | 0.68163 | 1 | 57226.508 | 6853.7058 | 8273.7084 | 2077.4237 | NORMAL
311.8537 | 0.33333 | 305.3722 | 0.68163 | 1 | 73773.932 | 7008.1539 | 8175.9925 | 2081.0325 | NORMAL
311.8537 | 0.33333 | 305.3722 | 0.68163 | 1 | 90321.356 | 7166.4028 | 8127.7775 | 2083.0167 | NORMAL
311.8537 | 0.33333 | 305.3722 | 0.68163 | 1 | 106868.78 | 7324.0639 | 8111.8702 | 2083.1885 | NORMAL
311.8537 | 0.33333 | 305.3722 | 0.68163 | 2 | 57226.508 | 10014.0815 | 10205.8352 | 3175.9988 | NORMAL
311.8537 | 0.33333 | 305.3722 | 0.68163 | 2 | 73773.932 | 10239.7485 | 10206.3173 | 3181.5161 | NORMAL
311.8537 | 0.33333 | 305.3722 | 0.68163 | 2 | 90321.356 | 10470.9691 | 10257.7284 | 3184.5496 | NORMAL
311.8537 | 0.33333 | 305.3722 | 0.68163 | 2 | 106868.78 | 10701.3307 | 10341.042 | 3184.8122 | NORMAL
311.8537 | 0.33333 | 305.3722 | 0.84923 | 1 | 57226.508 | 6606.5249 | 8868.2385 | 2042.4303 | NORMAL
311.8537 | 0.33333 | 305.3722 | 0.84923 | 1 | 73773.932 | 6755.4028 | 8709.2447 | 2045.9783 | NORMAL
311.8537 | 0.33333 | 305.3722 | 0.84923 | 1 | 90321.356 | 6907.9445 | 8608.0751 | 2047.9291 | NORMAL
311.8537 | 0.33333 | 305.3722 | 0.84923 | 1 | 106868.78 | 7059.9194 | 8545.2132 | 2048.098 | NORMAL
311.8537 | 0.33333 | 305.3722 | 0.84923 | 2 | 57226.508 | 9674.1792 | 11129.2828 | 3156.6979 | NORMAL
311.8537 | 0.33333 | 305.3722 | 0.84923 | 2 | 73773.932 | 9892.1865 | 11032.1654 | 3162.1816 | NORMAL
311.8537 | 0.33333 | 305.3722 | 0.84923 | 2 | 90321.356 | 10115.559 | 10998.6899 | 3165.1967 | NORMAL
311.8537 | 0.33333 | 305.3722 | 0.84923 | 2 | 106868.78 | 10338.1015 | 11006.383 | 3165.4577 | NORMAL
311.8537 | 0.66667 | 291.4833 | 0.34644 | 1 | 57226.508 | 7162.8207 | 3590.7113 | 2033.4333 | NORMAL
311.8537 | 0.66667 | 291.4833 | 0.34644 | 1 | 73773.932 | 7150.2612 | 3913.8031 | 2032.7133 | NORMAL
311.8537 | 0.66667 | 291.4833 | 0.34644 | 1 | 90321.356 | 7143.8255 | 4194.1727 | 2031.8451 | NORMAL
311.8537 | 0.66667 | 291.4833 | 0.34644 | 1 | 106868.78 | 7141.453 | 4436.888 | 2031.275 | NORMAL
311.8537 | 0.66667 | 291.4833 | 0.34644 | 2 | 57226.508 | 9717.5652 | 4572.218 | 2739.3714 | NORMAL
311.8537 | 0.66667 | 291.4833 | 0.34644 | 2 | 73773.932 | 9700.5262 | 5083.9208 | 2738.4014 | NORMAL
311.8537 | 0.66667 | 291.4833 | 0.34644 | 2 | 90321.356 | 9691.7951 | 5524.1916 | 2737.2319 | NORMAL
311.8537 | 0.66667 | 291.4833 | 0.34644 | 2 | 106868.78 | 9688.5764 | 5901.4917 | 2736.4639 | NORMAL
311.8537 | 0.66667 | 291.4833 | 0.51403 | 1 | 57226.508 | 6869.317 | 3861.8582 | 2094.8152 | NORMAL
311.8537 | 0.66667 | 291.4833 | 0.51403 | 1 | 73773.932 | 6857.2722 | 4108.1659 | 2094.0734 | NORMAL
311.8537 | 0.66667 | 291.4833 | 0.51403 | 1 | 90321.356 | 6851.1002 | 4324.1921 | 2093.1791 | NORMAL
311.8537 | 0.66667 | 291.4833 | 0.51403 | 1 | 106868.78 | 6848.8249 | 4512.9596 | 2092.5918 | NORMAL
311.8537 | 0.66667 | 291.4833 | 0.51403 | 2 | 57226.508 | 9905.0924 | 5060.6188 | 3111.3389 | NORMAL
311.8537 | 0.66667 | 291.4833 | 0.51403 | 2 | 73773.932 | 9887.7245 | 5490.0354 | 3110.2372 | NORMAL
311.8537 | 0.66667 | 291.4833 | 0.51403 | 2 | 90321.356 | 9878.825 | 5863.3668 | 3108.9089 | NORMAL
311.8537 | 0.66667 | 291.4833 | 0.51403 | 2 | 106868.78 | 9875.5441 | 6187.1824 | 3108.0366 | NORMAL
311.8537 | 0.66667 | 291.4833 | 0.68163 | 1 | 57226.508 | 6563.1764 | 4040.8922 | 2070.3847 | NORMAL
311.8537 | 0.66667 | 291.4833 | 0.68163 | 1 | 73773.932 | 6551.6683 | 4235.3474 | 2069.6516 | NORMAL
311.8537 | 0.66667 | 291.4833 | 0.68163 | 1 | 90321.356 | 6545.7714 | 4407.5918 | 2068.7677 | NORMAL
311.8537 | 0.66667 | 291.4833 | 0.68163 | 1 | 106868.78 | 6543.5975 | 4559.0473 | 2068.1873 | NORMAL
311.8537 | 0.66667 | 291.4833 | 0.68163 | 2 | 57226.508 | 9589.5833 | 5332.3235 | 3165.2376 | NORMAL
311.8537 | 0.66667 | 291.4833 | 0.68163 | 2 | 73773.932 | 9572.7687 | 5683.7459 | 3164.1168 | NORMAL
311.8537 | 0.66667 | 291.4833 | 0.68163 | 2 | 90321.356 | 9564.1526 | 5991.6444 | 3162.7655 | NORMAL
311.8537 | 0.66667 | 291.4833 | 0.68163 | 2 | 106868.78 | 9560.9763 | 6260.4883 | 3161.8781 | NORMAL
311.8537 | 0.66667 | 291.4833 | 0.84923 | 1 | 57226.508 | 6326.4736 | 4173.0379 | 2035.5099 | NORMAL
311.8537 | 0.66667 | 291.4833 | 0.84923 | 1 | 73773.932 | 6315.3805 | 4331.6786 | 2034.7892 | NORMAL
311.8537 | 0.66667 | 291.4833 | 0.84923 | 1 | 90321.356 | 6309.6963 | 4473.6436 | 2033.9201 | NORMAL
311.8537 | 0.66667 | 291.4833 | 0.84923 | 1 | 106868.78 | 6307.6008 | 4599.1632 | 2033.3494 | NORMAL
311.8537 | 0.66667 | 291.4833 | 0.84923 | 2 | 57226.508 | 9264.0896 | 5534.9237 | 3146.0021 | NORMAL
311.8537 | 0.66667 | 291.4833 | 0.84923 | 2 | 73773.932 | 9247.8456 | 5828.065 | 3144.8881 | NORMAL
311.8537 | 0.66667 | 291.4833 | 0.84923 | 2 | 90321.356 | 9239.522 | 6086.7903 | 3143.545 | NORMAL
311.8537 | 0.66667 | 291.4833 | 0.84923 | 2 | 106868.78 | 9236.4535 | 6313.8059 | 3142.663 | NORMAL
311.8537 | 0.66667 | 296.113 | 0.34644 | 1 | 57226.508 | 7403.6337 | 3417.9209 | 2038.2529 | NORMAL
311.8537 | 0.66667 | 296.113 | 0.34644 | 1 | 73773.932 | 7455.9854 | 3731.263 | 2039.7208 | NORMAL
311.8537 | 0.66667 | 296.113 | 0.34644 | 1 | 90321.356 | 7505.7548 | 4021.1578 | 2040.9905 | NORMAL
311.8537 | 0.66667 | 296.113 | 0.34644 | 1 | 106868.78 | 7552.8449 | 4286.7697 | 2042.0718 | NORMAL
311.8537 | 0.66667 | 296.113 | 0.34644 | 2 | 57226.508 | 10044.2685 | 4256.2006 | 2745.8642 | NORMAL
311.8537 | 0.66667 | 296.113 | 0.34644 | 2 | 73773.932 | 10115.2922 | 4752.6756 | 2747.8418 | NORMAL
311.8537 | 0.66667 | 296.113 | 0.34644 | 2 | 90321.356 | 10182.8128 | 5209.8816 | 2749.5521 | NORMAL
311.8537 | 0.66667 | 296.113 | 0.34644 | 2 | 106868.78 | 10246.6984 | 5626.2697 | 2751.0089 | NORMAL
311.8537 | 0.66667 | 296.113 | 0.51403 | 1 | 57226.508 | 7100.2625 | 3772.8108 | 2099.7803 | NORMAL
311.8537 | 0.66667 | 296.113 | 0.51403 | 1 | 73773.932 | 7150.469 | 4011.7006 | 2101.2925 | NORMAL
311.8537 | 0.66667 | 296.113 | 0.51403 | 1 | 90321.356 | 7198.1991 | 4235.3733 | 2102.6004 | NORMAL
311.8537 | 0.66667 | 296.113 | 0.51403 | 1 | 106868.78 | 7243.3596 | 4442.2205 | 2103.7144 | NORMAL
311.8537 | 0.66667 | 296.113 | 0.51403 | 2 | 57226.508 | 10238.1003 | 4841.8858 | 3118.7134 | NORMAL
311.8537 | 0.66667 | 296.113 | 0.51403 | 2 | 73773.932 | 10310.4946 | 5258.3534 | 3120.9594 | NORMAL
311.8537 | 0.66667 | 296.113 | 0.51403 | 2 | 90321.356 | 10379.3182 | 5644.2674 | 3122.902 | NORMAL
311.8537 | 0.66667 | 296.113 | 0.51403 | 2 | 106868.78 | 10444.4366 | 5998.3795 | 3124.5566 | NORMAL
311.8537 | 0.66667 | 296.113 | 0.68163 | 1 | 57226.508 | 6783.8295 | 4008.4024 | 2075.2919 | NORMAL
311.8537 | 0.66667 | 296.113 | 0.68163 | 1 | 73773.932 | 6831.7984 | 4196.9049 | 2076.7865 | NORMAL
311.8537 | 0.66667 | 296.113 | 0.68163 | 1 | 90321.356 | 6877.4014 | 4376.0959 | 2078.0792 | NORMAL
311.8537 | 0.66667 | 296.113 | 0.68163 | 1 | 106868.78 | 6920.5493 | 4543.4171 | 2079.1802 | NORMAL
311.8537 | 0.66667 | 296.113 | 0.68163 | 2 | 57226.508 | 9911.9838 | 5198.5179 | 3172.7398 | NORMAL
311.8537 | 0.66667 | 296.113 | 0.68163 | 2 | 73773.932 | 9982.0722 | 5539.3628 | 3175.0248 | NORMAL
311.8537 | 0.66667 | 296.113 | 0.68163 | 2 | 90321.356 | 10048.7035 | 5858.0395 | 3177.001 | NORMAL
311.8537 | 0.66667 | 296.113 | 0.68163 | 2 | 106868.78 | 10111.7477 | 6152.4564 | 3178.6843 | NORMAL
311.8537 | 0.66667 | 296.113 | 0.84923 | 1 | 57226.508 | 6539.1687 | 4180.0157 | 2040.3345 | NORMAL
311.8537 | 0.66667 | 296.113 | 0.84923 | 1 | 73773.932 | 6585.4077 | 4333.647 | 2041.8039 | NORMAL
311.8537 | 0.66667 | 296.113 | 0.84923 | 1 | 90321.356 | 6629.3659 | 4482.2073 | 2043.0748 | NORMAL
311.8537 | 0.66667 | 296.113 | 0.84923 | 1 | 106868.78 | 6670.9577 | 4622.3422 | 2044.1572 | NORMAL
311.8537 | 0.66667 | 296.113 | 0.84923 | 2 | 57226.508 | 9575.547 | 5464.7045 | 3153.4587 | NORMAL
311.8537 | 0.66667 | 296.113 | 0.84923 | 2 | 73773.932 | 9643.2564 | 5748.9436 | 3155.7298 | NORMAL
311.8537 | 0.66667 | 296.113 | 0.84923 | 2 | 90321.356 | 9707.6261 | 6017.5913 | 3157.694 | NORMAL
311.8537 | 0.66667 | 296.113 | 0.84923 | 2 | 106868.78 | 9768.5304 | 6267.551 | 3159.3671 | NORMAL
311.8537 | 0.66667 | 300.7426 | 0.34644 | 1 | 57226.508 | 8520.0703 | 3478.0307 | 2035.1886 | NORMAL
311.8537 | 0.66667 | 300.7426 | 0.34644 | 1 | 73773.932 | 8627.8337 | 3815.629 | 2033.467 | NORMAL
311.8537 | 0.66667 | 300.7426 | 0.34644 | 1 | 90321.356 | 8727.1368 | 4143.9491 | 2033.467 | NORMAL
311.8537 | 0.66667 | 300.7426 | 0.34644 | 1 | 106868.78 | 8819.4913 | 4457.2154 | 2033.467 | NORMAL
311.8537 | 0.66667 | 300.7426 | 0.34644 | 2 | 57226.508 | 11558.9015 | 4281.0486 | 2741.7361 | NORMAL
311.8537 | 0.66667 | 300.7426 | 0.34644 | 2 | 73773.932 | 11705.1007 | 4814.3483 | 2739.4168 | NORMAL
311.8537 | 0.66667 | 300.7426 | 0.34644 | 2 | 90321.356 | 11839.8219 | 5331.8685 | 2739.4168 | NORMAL
311.8537 | 0.66667 | 300.7426 | 0.34644 | 2 | 106868.78 | 11965.1162 | 5824.656 | 2739.4168 | NORMAL
311.8537 | 0.66667 | 300.7426 | 0.51403 | 1 | 57226.508 | 8170.9519 | 3892.1705 | 2096.6235 | NORMAL
311.8537 | 0.66667 | 300.7426 | 0.51403 | 1 | 73773.932 | 8274.2997 | 4152.4022 | 2094.8498 | NORMAL
311.8537 | 0.66667 | 300.7426 | 0.51403 | 1 | 90321.356 | 8369.5338 | 4408.8345 | 2094.8498 | NORMAL
311.8537 | 0.66667 | 300.7426 | 0.51403 | 1 | 106868.78 | 8458.1039 | 4655.2282 | 2094.8498 | NORMAL
311.8537 | 0.66667 | 300.7426 | 0.51403 | 2 | 57226.508 | 11781.9623 | 4940.3627 | 3114.0247 | NORMAL
311.8537 | 0.66667 | 300.7426 | 0.51403 | 2 | 73773.932 | 11930.9828 | 5389.6964 | 3111.3904 | NORMAL
311.8537 | 0.66667 | 300.7426 | 0.51403 | 2 | 90321.356 | 12068.3039 | 5827.3162 | 3111.3904 | NORMAL
311.8537 | 0.66667 | 300.7426 | 0.51403 | 2 | 106868.78 | 12196.0161 | 6245.2207 | 3111.3904 | NORMAL
311.8537 | 0.66667 | 300.7426 | 0.68163 | 1 | 57226.508 | 7806.8022 | 4168.6275 | 2072.1719 | NORMAL
311.8537 | 0.66667 | 300.7426 | 0.68163 | 1 | 73773.932 | 7905.5441 | 4376.8516 | 2070.419 | NORMAL
311.8537 | 0.66667 | 300.7426 | 0.68163 | 1 | 90321.356 | 7996.5339 | 4585.8862 | 2070.419 | NORMAL
311.8537 | 0.66667 | 300.7426 | 0.68163 | 1 | 106868.78 | 8081.1568 | 4788.6359 | 2070.419 | NORMAL
311.8537 | 0.66667 | 300.7426 | 0.68163 | 2 | 57226.508 | 11406.6689 | 5357.0766 | 3167.9699 | NORMAL
311.8537 | 0.66667 | 300.7426 | 0.68163 | 2 | 73773.932 | 11550.9426 | 5727.8781 | 3165.29 | NORMAL
311.8537 | 0.66667 | 300.7426 | 0.68163 | 2 | 90321.356 | 11683.8896 | 6092.6394 | 3165.29 | NORMAL
311.8537 | 0.66667 | 300.7426 | 0.68163 | 2 | 106868.78 | 11807.5337 | 6442.8119 | 3165.29 | NORMAL
311.8537 | 0.66667 | 300.7426 | 0.84923 | 1 | 57226.508 | 7525.2476 | 4369.4023 | 2037.267 | NORMAL
311.8537 | 0.66667 | 300.7426 | 0.84923 | 1 | 73773.932 | 7620.4284 | 4541.7503 | 2035.5436 | NORMAL
311.8537 | 0.66667 | 300.7426 | 0.84923 | 1 | 90321.356 | 7708.1366 | 4718.4236 | 2035.5436 | NORMAL
311.8537 | 0.66667 | 300.7426 | 0.84923 | 1 | 106868.78 | 7789.7076 | 4891.5583 | 2035.5436 | NORMAL
311.8537 | 0.66667 | 300.7426 | 0.84923 | 2 | 57226.508 | 11019.4988 | 5669.1036 | 3148.7178 | NORMAL
311.8537 | 0.66667 | 300.7426 | 0.84923 | 2 | 73773.932 | 11158.8755 | 5981.4339 | 3146.0542 | NORMAL
311.8537 | 0.66667 | 300.7426 | 0.84923 | 2 | 90321.356 | 11287.31 | 6292.7628 | 3146.0542 | NORMAL
311.8537 | 0.66667 | 300.7426 | 0.84923 | 2 | 106868.78 | 11406.7573 | 6593.6578 | 3146.0542 | NORMAL
311.8537 | 0.66667 | 305.3722 | 0.34644 | 1 | 57226.508 | 10525.0545 | 3663.3536 | 2033.467 | NORMAL
311.8537 | 0.66667 | 305.3722 | 0.34644 | 1 | 73773.932 | 10677.2673 | 4047.3724 | 2033.467 | NORMAL
311.8537 | 0.66667 | 305.3722 | 0.34644 | 1 | 90321.356 | 10818.313 | 4435.0228 | 2033.467 | NORMAL
311.8537 | 0.66667 | 305.3722 | 0.34644 | 1 | 106868.78 | 10949.4571 | 4817.2452 | 2033.467 | NORMAL
311.8537 | 0.66667 | 305.3722 | 0.34644 | 2 | 57226.508 | 14278.9982 | 4486.3162 | 2739.4168 | NORMAL
311.8537 | 0.66667 | 305.3722 | 0.34644 | 2 | 73773.932 | 14485.5003 | 5092.2357 | 2739.4168 | NORMAL
311.8537 | 0.66667 | 305.3722 | 0.34644 | 2 | 90321.356 | 14676.8525 | 5704.8191 | 2739.4168 | NORMAL
311.8537 | 0.66667 | 305.3722 | 0.34644 | 2 | 106868.78 | 14854.7713 | 6310.1687 | 2739.4168 | NORMAL
311.8537 | 0.66667 | 305.3722 | 0.51403 | 1 | 57226.508 | 10093.78 | 4125.795 | 2094.8498 | NORMAL
311.8537 | 0.66667 | 305.3722 | 0.51403 | 1 | 73773.932 | 10239.7557 | 4425.0747 | 2094.8498 | NORMAL
311.8537 | 0.66667 | 305.3722 | 0.51403 | 1 | 90321.356 | 10375.0219 | 4730.7121 | 2094.8498 | NORMAL
311.8537 | 0.66667 | 305.3722 | 0.51403 | 1 | 106868.78 | 10500.7922 | 5033.383 | 2094.8498 | NORMAL
311.8537 | 0.66667 | 305.3722 | 0.51403 | 2 | 57226.508 | 14554.5508 | 5210.0154 | 3111.3904 | NORMAL
311.8537 | 0.66667 | 305.3722 | 0.51403 | 2 | 73773.932 | 14765.038 | 5721.7442 | 3111.3904 | NORMAL
311.8537 | 0.66667 | 305.3722 | 0.51403 | 2 | 90321.356 | 14960.0828 | 6238.7938 | 3111.3904 | NORMAL
311.8537 | 0.66667 | 305.3722 | 0.51403 | 2 | 106868.78 | 15141.4351 | 6748.6729 | 3111.3904 | NORMAL
311.8537 | 0.66667 | 305.3722 | 0.68163 | 1 | 57226.508 | 9643.9367 | 4435.8885 | 2070.419 | NORMAL
311.8537 | 0.66667 | 305.3722 | 0.68163 | 1 | 73773.932 | 9783.4068 | 4679.0487 | 2070.419 | NORMAL
311.8537 | 0.66667 | 305.3722 | 0.68163 | 1 | 90321.356 | 9912.6447 | 4932.0678 | 2070.419 | NORMAL
311.8537 | 0.66667 | 305.3722 | 0.68163 | 1 | 106868.78 | 10032.8099 | 5184.821 | 2070.419 | NORMAL
311.8537 | 0.66667 | 305.3722 | 0.68163 | 2 | 57226.508 | 14090.9415 | 5675.6654 | 3165.29 | NORMAL
311.8537 | 0.66667 | 305.3722 | 0.68163 | 2 | 73773.932 | 14294.724 | 6101.4982 | 3165.29 | NORMAL
311.8537 | 0.66667 | 305.3722 | 0.68163 | 2 | 90321.356 | 14483.556 | 6535.6448 | 3165.29 | NORMAL
311.8537 | 0.66667 | 305.3722 | 0.68163 | 2 | 106868.78 | 14659.1316 | 6965.2568 | 3165.29 | NORMAL
311.8537 | 0.66667 | 305.3722 | 0.84923 | 1 | 57226.508 | 9296.1253 | 4661.0381 | 2035.5436 | NORMAL
311.8537 | 0.66667 | 305.3722 | 0.84923 | 1 | 73773.932 | 9430.5654 | 4865.7585 | 2035.5436 | NORMAL
311.8537 | 0.66667 | 305.3722 | 0.84923 | 1 | 90321.356 | 9555.1424 | 5083.3023 | 2035.5436 | NORMAL
311.8537 | 0.66667 | 305.3722 | 0.84923 | 1 | 106868.78 | 9670.9737 | 5302.7881 | 2035.5436 | NORMAL
311.8537 | 0.66667 | 305.3722 | 0.84923 | 2 | 57226.508 | 13612.6607 | 6025.3981 | 3146.0542 | NORMAL
311.8537 | 0.66667 | 305.3722 | 0.84923 | 2 | 73773.932 | 13809.5263 | 6388.0176 | 3146.0542 | NORMAL
311.8537 | 0.66667 | 305.3722 | 0.84923 | 2 | 90321.356 | 13991.9489 | 6762.6372 | 3146.0542 | NORMAL
311.8537 | 0.66667 | 305.3722 | 0.84923 | 2 | 106868.78 | 14161.565 | 7135.5973 | 3146.0542 | NORMAL
311.8537 | 1 | 291.4833 | 0.34644 | 1 | 57226.508 | 7475.5198 | 1769.61 | 2040.2343 | NORMAL
311.8537 | 1 | 291.4833 | 0.34644 | 1 | 73773.932 | 7475.5198 | 2205.1387 | 2040.2343 | NORMAL
311.8537 | 1 | 291.4833 | 0.34644 | 1 | 90321.356 | 7475.5198 | 2597.4076 | 2040.2343 | NORMAL
311.8537 | 1 | 291.4833 | 0.34644 | 1 | 106868.78 | 7475.5198 | 2948.9689 | 2040.2343 | NORMAL
311.8537 | 1 | 291.4833 | 0.34644 | 2 | 57226.508 | 10141.7939 | 2486.1545 | 2748.5335 | NORMAL
311.8537 | 1 | 291.4833 | 0.34644 | 2 | 73773.932 | 10141.7939 | 3117.5294 | 2748.5335 | NORMAL
311.8537 | 1 | 291.4833 | 0.34644 | 2 | 90321.356 | 10141.7939 | 3687.6467 | 2748.5335 | NORMAL
311.8537 | 1 | 291.4833 | 0.34644 | 2 | 106868.78 | 10141.7939 | 4197.4352 | 2748.5335 | NORMAL
311.8537 | 1 | 291.4833 | 0.51403 | 1 | 57226.508 | 7169.203 | 1643.466 | 2101.8214 | NORMAL
311.8537 | 1 | 291.4833 | 0.51403 | 1 | 73773.932 | 7169.203 | 2036.3397 | 2101.8214 | NORMAL
311.8537 | 1 | 291.4833 | 0.51403 | 1 | 90321.356 | 7169.203 | 2389.0316 | 2101.8214 | NORMAL
311.8537 | 1 | 291.4833 | 0.51403 | 1 | 106868.78 | 7169.203 | 2705.299 | 2101.8214 | NORMAL
311.8537 | 1 | 291.4833 | 0.51403 | 2 | 57226.508 | 10337.5078 | 2430.0043 | 3121.745 | NORMAL
311.8537 | 1 | 291.4833 | 0.51403 | 2 | 73773.932 | 10337.5078 | 3024.2862 | 3121.745 | NORMAL
311.8537 | 1 | 291.4833 | 0.51403 | 2 | 90321.356 | 10337.5078 | 3559.1916 | 3121.745 | NORMAL
311.8537 | 1 | 291.4833 | 0.51403 | 2 | 106868.78 | 10337.5078 | 4038.6994 | 3121.745 | NORMAL
311.8537 | 1 | 291.4833 | 0.68163 | 1 | 57226.508 | 6849.6975 | 1546.2503 | 2077.3093 | NORMAL
311.8537 | 1 | 291.4833 | 0.68163 | 1 | 73773.932 | 6849.6975 | 1910.7463 | 2077.3093 | NORMAL
311.8537 | 1 | 291.4833 | 0.68163 | 1 | 90321.356 | 6849.6975 | 2237.3734 | 2077.3093 | NORMAL
311.8537 | 1 | 291.4833 | 0.68163 | 1 | 106868.78 | 6849.6975 | 2530.2244 | 2077.3093 | NORMAL
311.8537 | 1 | 291.4833 | 0.68163 | 2 | 57226.508 | 10008.2249 | 2299.5311 | 3175.824 | NORMAL
311.8537 | 1 | 291.4833 | 0.68163 | 2 | 73773.932 | 10008.2249 | 2850.3816 | 3175.824 | NORMAL
311.8537 | 1 | 291.4833 | 0.68163 | 2 | 90321.356 | 10008.2249 | 3345.0198 | 3175.824 | NORMAL
311.8537 | 1 | 291.4833 | 0.68163 | 2 | 106868.78 | 10008.2249 | 3788.5745 | 3175.824 | NORMAL
311.8537 | 1 | 291.4833 | 0.84923 | 1 | 57226.508 | 6602.6612 | 1477.5488 | 2042.3178 | NORMAL
311.8537 | 1 | 291.4833 | 0.84923 | 1 | 73773.932 | 6602.6612 | 1823.0972 | 2042.3178 | NORMAL
311.8537 | 1 | 291.4833 | 0.84923 | 1 | 90321.356 | 6602.6612 | 2132.4128 | 2042.3178 | NORMAL
311.8537 | 1 | 291.4833 | 0.84923 | 1 | 106868.78 | 6602.6612 | 2409.6915 | 2042.3178 | NORMAL
311.8537 | 1 | 291.4833 | 0.84923 | 2 | 57226.508 | 9668.5214 | 2192.4077 | 3156.5241 | NORMAL
311.8537 | 1 | 291.4833 | 0.84923 | 2 | 73773.932 | 9668.5214 | 2711.3413 | 3156.5241 | NORMAL
311.8537 | 1 | 291.4833 | 0.84923 | 2 | 90321.356 | 9668.5214 | 3176.6119 | 3156.5241 | NORMAL
311.8537 | 1 | 291.4833 | 0.84923 | 2 | 106868.78 | 9668.5214 | 3593.7977 | 3156.5241 | NORMAL
311.8537 | 1 | 296.113 | 0.34644 | 1 | 57226.508 | 8858.2388 | 1684.2911 | 2033.467 | NORMAL
311.8537 | 1 | 296.113 | 0.34644 | 1 | 73773.932 | 8858.2388 | 2134.9145 | 2033.467 | NORMAL
311.8537 | 1 | 296.113 | 0.34644 | 1 | 90321.356 | 8858.2388 | 2554.3666 | 2033.467 | NORMAL
311.8537 | 1 | 296.113 | 0.34644 | 1 | 106868.78 | 8858.2388 | 2942.1714 | 2033.467 | NORMAL
311.8537 | 1 | 296.113 | 0.34644 | 2 | 57226.508 | 12017.6838 | 2362.9777 | 2739.4168 | NORMAL
311.8537 | 1 | 296.113 | 0.34644 | 2 | 73773.932 | 12017.6838 | 3018.5433 | 2739.4168 | NORMAL
311.8537 | 1 | 296.113 | 0.34644 | 2 | 90321.356 | 12017.6838 | 3633.5206 | 2739.4168 | NORMAL
311.8537 | 1 | 296.113 | 0.34644 | 2 | 106868.78 | 12017.6838 | 4203.7178 | 2739.4168 | NORMAL
311.8537 | 1 | 296.113 | 0.51403 | 1 | 57226.508 | 8495.2637 | 1566.4028 | 2094.8498 | NORMAL
311.8537 | 1 | 296.113 | 0.51403 | 1 | 73773.932 | 8495.2637 | 1971.8995 | 2094.8498 | NORMAL
311.8537 | 1 | 296.113 | 0.51403 | 1 | 90321.356 | 8495.2637 | 2346.5677 | 2094.8498 | NORMAL
311.8537 | 1 | 296.113 | 0.51403 | 1 | 106868.78 | 8495.2637 | 2691.7231 | 2094.8498 | NORMAL
311.8537 | 1 | 296.113 | 0.51403 | 2 | 57226.508 | 12249.5981 | 2313.5289 | 3111.3904 | NORMAL
311.8537 | 1 | 296.113 | 0.51403 | 2 | 73773.932 | 12249.5981 | 2928.0422 | 3111.3904 | NORMAL
311.8537 | 1 | 296.113 | 0.51403 | 2 | 90321.356 | 12249.5981 | 3499.1317 | 3111.3904 | NORMAL
311.8537 | 1 | 296.113 | 0.51403 | 2 | 106868.78 | 12249.5981 | 4026.753 | 3111.3904 | NORMAL
311.8537 | 1 | 296.113 | 0.68163 | 1 | 57226.508 | 8116.6606 | 1474.7709 | 2070.419 | NORMAL
311.8537 | 1 | 296.113 | 0.68163 | 1 | 73773.932 | 8116.6606 | 1850.6261 | 2070.419 | NORMAL
311.8537 | 1 | 296.113 | 0.68163 | 1 | 90321.356 | 8116.6606 | 2196.6717 | 2070.419 | NORMAL
311.8537 | 1 | 296.113 | 0.68163 | 1 | 106868.78 | 8116.6606 | 2514.8398 | 2070.419 | NORMAL
311.8537 | 1 | 296.113 | 0.68163 | 2 | 57226.508 | 11859.4089 | 2191.4816 | 3165.29 | NORMAL
311.8537 | 1 | 296.113 | 0.68163 | 2 | 73773.932 | 11859.4089 | 2760.1171 | 3165.29 | NORMAL
311.8537 | 1 | 296.113 | 0.68163 | 2 | 90321.356 | 11859.4089 | 3285.7989 | 3165.29 | NORMAL
311.8537 | 1 | 296.113 | 0.68163 | 2 | 106868.78 | 11859.4089 | 3770.2077 | 3165.29 | NORMAL
311.8537 | 1 | 296.113 | 0.84923 | 1 | 57226.508 | 7823.9309 | 1409.812 | 2035.5436 | NORMAL
311.8537 | 1 | 296.113 | 0.84923 | 1 | 73773.932 | 7823.9309 | 1765.9619 | 2035.5436 | NORMAL
311.8537 | 1 | 296.113 | 0.84923 | 1 | 90321.356 | 7823.9309 | 2093.2056 | 2035.5436 | NORMAL
311.8537 | 1 | 296.113 | 0.84923 | 1 | 106868.78 | 7823.9309 | 2393.7415 | 2035.5436 | NORMAL
311.8537 | 1 | 296.113 | 0.84923 | 2 | 57226.508 | 11456.8718 | 2090.6291 | 3146.0542 | NORMAL
311.8537 | 1 | 296.113 | 0.84923 | 2 | 73773.932 | 11456.8718 | 2625.8733 | 3146.0542 | NORMAL
311.8537 | 1 | 296.113 | 0.84923 | 2 | 90321.356 | 11456.8718 | 3119.1795 | 3146.0542 | NORMAL
311.8537 | 1 | 296.113 | 0.84923 | 2 | 106868.78 | 11456.8718 | 3573.008 | 3146.0542 | NORMAL
311.8537 | 1 | 300.7426 | 0.34644 | 1 | 57226.508 | 11313.2402 | 1731.817 | 2033.467 | NORMAL
311.8537 | 1 | 300.7426 | 0.34644 | 1 | 73773.932 | 11313.2402 | 2233.3596 | 2033.467 | NORMAL
311.8537 | 1 | 300.7426 | 0.34644 | 1 | 90321.356 | 11313.2402 | 2714.6826 | 2033.467 | NORMAL
311.8537 | 1 | 300.7426 | 0.34644 | 1 | 106868.78 | 11313.2402 | 3172.948 | 2033.467 | NORMAL
311.8537 | 1 | 300.7426 | 0.34644 | 2 | 57226.508 | 15348.304 | 2431.9844 | 2739.4168 | NORMAL
311.8537 | 1 | 300.7426 | 0.34644 | 2 | 73773.932 | 15348.304 | 3167.2412 | 2739.4168 | NORMAL
311.8537 | 1 | 300.7426 | 0.34644 | 2 | 90321.356 | 15348.304 | 3882.4509 | 2739.4168 | NORMAL
311.8537 | 1 | 300.7426 | 0.34644 | 2 | 106868.78 | 15348.304 | 4569.2388 | 2739.4168 | NORMAL
311.8537 | 1 | 300.7426 | 0.51403 | 1 | 57226.508 | 10849.6689 | 1609.54 | 2094.8498 | NORMAL
311.8537 | 1 | 300.7426 | 0.51403 | 1 | 73773.932 | 10849.6689 | 2058.1456 | 2094.8498 | NORMAL
311.8537 | 1 | 300.7426 | 0.51403 | 1 | 90321.356 | 10849.6689 | 2483.5793 | 2094.8498 | NORMAL
311.8537 | 1 | 300.7426 | 0.51403 | 1 | 106868.78 | 10849.6689 | 2885.337 | 2094.8498 | NORMAL
311.8537 | 1 | 300.7426 | 0.51403 | 2 | 57226.508 | 15644.4918 | 2378.4261 | 3111.3904 | NORMAL
311.8537 | 1 | 300.7426 | 0.51403 | 2 | 73773.932 | 15644.4918 | 3061.4243 | 3111.3904 | NORMAL
311.8537 | 1 | 300.7426 | 0.51403 | 2 | 90321.356 | 15644.4918 | 3715.1569 | 3111.3904 | NORMAL
311.8537 | 1 | 300.7426 | 0.51403 | 2 | 106868.78 | 15644.4918 | 4336.469 | 3111.3904 | NORMAL
311.8537 | 1 | 300.7426 | 0.68163 | 1 | 57226.508 | 10366.1384 | 1515.0118 | 2070.419 | NORMAL
311.8537 | 1 | 300.7426 | 0.68163 | 1 | 73773.932 | 10366.1384 | 1929.7561 | 2070.419 | NORMAL
311.8537 | 1 | 300.7426 | 0.68163 | 1 | 90321.356 | 10366.1384 | 2320.9303 | 2070.419 | NORMAL
311.8537 | 1 | 300.7426 | 0.68163 | 1 | 106868.78 | 10366.1384 | 2688.8968 | 2070.419 | NORMAL
311.8537 | 1 | 300.7426 | 0.68163 | 2 | 57226.508 | 15146.1644 | 2251.9237 | 3165.29 | NORMAL
311.8537 | 1 | 300.7426 | 0.68163 | 2 | 73773.932 | 15146.1644 | 2881.2625 | 3165.29 | NORMAL
311.8537 | 1 | 300.7426 | 0.68163 | 2 | 90321.356 | 15146.1644 | 3478.587 | 3165.29 | NORMAL
311.8537 | 1 | 300.7426 | 0.68163 | 2 | 106868.78 | 15146.1644 | 4042.998 | 3165.29 | NORMAL
311.8537 | 1 | 300.7426 | 0.84923 | 1 | 57226.508 | 9992.2807 | 1448.1063 | 2035.5436 | NORMAL
311.8537 | 1 | 300.7426 | 0.84923 | 1 | 73773.932 | 9992.2807 | 1840.5671 | 2035.5436 | NORMAL
311.8537 | 1 | 300.7426 | 0.84923 | 1 | 90321.356 | 9992.2807 | 2209.6032 | 2035.5436 | NORMAL
311.8537 | 1 | 300.7426 | 0.84923 | 1 | 106868.78 | 9992.2807 | 2555.9855 | 2035.5436 | NORMAL
311.8537 | 1 | 300.7426 | 0.84923 | 2 | 57226.508 | 14632.0667 | 2147.8192 | 3146.0542 | NORMAL
311.8537 | 1 | 300.7426 | 0.84923 | 2 | 73773.932 | 14632.0667 | 2738.8768 | 3146.0542 | NORMAL
311.8537 | 1 | 300.7426 | 0.84923 | 2 | 90321.356 | 14632.0667 | 3297.2282 | 3146.0542 | NORMAL
311.8537 | 1 | 300.7426 | 0.84923 | 2 | 106868.78 | 14632.0667 | 3823.0507 | 3146.0542 | NORMAL
311.8537 | 1 | 305.3722 | 0.34644 | 1 | 57226.508 | 14840.5237 | 1824.7559 | 2033.467 | NORMAL
311.8537 | 1 | 305.3722 | 0.34644 | 1 | 73773.932 | 14840.5237 | 2394.299 | 2033.467 | NORMAL
311.8537 | 1 | 305.3722 | 0.34644 | 1 | 90321.356 | 14840.5237 | 2956.9045 | 2033.467 | NORMAL
311.8537 | 1 | 305.3722 | 0.34644 | 1 | 106868.78 | 14840.5237 | 3508.2337 | 2033.467 | NORMAL
311.8537 | 1 | 305.3722 | 0.34644 | 2 | 57226.508 | 20133.6546 | 2566.3167 | 2739.4168 | NORMAL
311.8537 | 1 | 305.3722 | 0.34644 | 2 | 73773.932 | 20133.6546 | 3408.8699 | 2739.4168 | NORMAL
311.8537 | 1 | 305.3722 | 0.34644 | 2 | 90321.356 | 20133.6546 | 4258.3219 | 2739.4168 | NORMAL
311.8537 | 1 | 305.3722 | 0.34644 | 2 | 106868.78 | 20133.6546 | 5104.1187 | 2739.4168 | NORMAL
311.8537 | 1 | 305.3722 | 0.51403 | 1 | 57226.508 | 14232.4186 | 1694.0869 | 2094.8498 | NORMAL
311.8537 | 1 | 305.3722 | 0.51403 | 1 | 73773.932 | 14232.4186 | 2199.9507 | 2094.8498 | NORMAL
311.8537 | 1 | 305.3722 | 0.51403 | 1 | 90321.356 | 14232.4186 | 2691.1945 | 2094.8498 | NORMAL
311.8537 | 1 | 305.3722 | 0.51403 | 1 | 106868.78 | 14232.4186 | 3166.0172 | 2094.8498 | NORMAL
311.8537 | 1 | 305.3722 | 0.51403 | 2 | 57226.508 | 20522.1889 | 2505.4182 | 3111.3904 | NORMAL
311.8537 | 1 | 305.3722 | 0.51403 | 2 | 73773.932 | 20522.1889 | 3279.7527 | 3111.3904 | NORMAL
311.8537 | 1 | 305.3722 | 0.51403 | 2 | 90321.356 | 20522.1889 | 4041.7048 | 3111.3904 | NORMAL
311.8537 | 1 | 305.3722 | 0.51403 | 2 | 106868.78 | 20522.1889 | 4786.0815 | 3111.3904 | NORMAL
311.8537 | 1 | 305.3722 | 0.68163 | 1 | 57226.508 | 13598.1311 | 1593.9132 | 2070.419 | NORMAL
311.8537 | 1 | 305.3722 | 0.68163 | 1 | 73773.932 | 13598.1311 | 2060.2079 | 2070.419 | NORMAL
311.8537 | 1 | 305.3722 | 0.68163 | 1 | 90321.356 | 13598.1311 | 2509.5893 | 2070.419 | NORMAL
311.8537 | 1 | 305.3722 | 0.68163 | 1 | 106868.78 | 13598.1311 | 2941.2661 | 2070.419 | NORMAL
311.8537 | 1 | 305.3722 | 0.68163 | 2 | 57226.508 | 19868.4911 | 2370.3759 | 3165.29 | NORMAL
311.8537 | 1 | 305.3722 | 0.68163 | 2 | 73773.932 | 19868.4911 | 3080.3687 | 3165.29 | NORMAL
311.8537 | 1 | 305.3722 | 0.68163 | 2 | 90321.356 | 19868.4911 | 3770.6437 | 3165.29 | NORMAL
311.8537 | 1 | 305.3722 | 0.68163 | 2 | 106868.78 | 19868.4911 | 4438.4738 | 3165.29 | NORMAL
311.8537 | 1 | 305.3722 | 0.84923 | 1 | 57226.508 | 13107.7106 | 1523.1929 | 2035.5436 | NORMAL
311.8537 | 1 | 305.3722 | 0.84923 | 1 | 73773.932 | 13107.7106 | 1963.7396 | 2035.5436 | NORMAL
311.8537 | 1 | 305.3722 | 0.84923 | 1 | 90321.356 | 13107.7106 | 2386.5441 | 2035.5436 | NORMAL
311.8537 | 1 | 305.3722 | 0.84923 | 1 | 106868.78 | 13107.7106 | 2791.3167 | 2035.5436 | NORMAL
311.8537 | 1 | 305.3722 | 0.84923 | 2 | 57226.508 | 19194.1062 | 2259.9456 | 3146.0542 | NORMAL
311.8537 | 1 | 305.3722 | 0.84923 | 2 | 73773.932 | 19194.1062 | 2925.0283 | 3146.0542 | NORMAL
311.8537 | 1 | 305.3722 | 0.84923 | 2 | 90321.356 | 19194.1062 | 3567.3928 | 3146.0542 | NORMAL
311.8537 | 1 | 305.3722 | 0.84923 | 2 | 106868.78 | 19194.1062 | 4185.5507 | 3146.0542 | NORMAL
324.8167 | 0 | 291.4833 | 0.34644 | 1 | 57226.508 | 11737.122 | 12483.1732 | 2677.7648 | NORMAL
324.8167 | 0 | 291.4833 | 0.34644 | 1 | 73773.932 | 10384.7474 | 11234.8283 | 2677.7648 | NORMAL
324.8167 | 0 | 291.4833 | 0.34644 | 1 | 90321.356 | 9482.0488 | 10379.3518 | 2677.7648 | NORMAL
324.8167 | 0 | 291.4833 | 0.34644 | 1 | 106868.78 | 8841.3445 | 9752.8527 | 2677.7648 | NORMAL
324.8167 | 0 | 291.4833 | 0.34644 | 2 | 57226.508 | 15923.3707 | 16257.9219 | 3607.3926 | NORMAL
324.8167 | 0 | 291.4833 | 0.34644 | 2 | 73773.932 | 14088.6481 | 14529.5433 | 3607.3926 | NORMAL
324.8167 | 0 | 291.4833 | 0.34644 | 2 | 90321.356 | 12863.9863 | 13371.4781 | 3607.3926 | NORMAL
324.8167 | 0 | 291.4833 | 0.34644 | 2 | 106868.78 | 11994.7637 | 12540.0011 | 3607.3926 | NORMAL
324.8167 | 0 | 291.4833 | 0.51403 | 1 | 57226.508 | 11256.1819 | 13194.1088 | 2758.5966 | NORMAL
324.8167 | 0 | 291.4833 | 0.51403 | 1 | 73773.932 | 9959.2221 | 11948.6442 | 2758.5966 | NORMAL
324.8167 | 0 | 291.4833 | 0.51403 | 1 | 90321.356 | 9093.5124 | 11066.7253 | 2758.5966 | NORMAL
324.8167 | 0 | 291.4833 | 0.51403 | 1 | 106868.78 | 8479.0616 | 10404.0516 | 2758.5966 | NORMAL
324.8167 | 0 | 291.4833 | 0.51403 | 2 | 57226.508 | 16230.656 | 17514.0042 | 4097.225 | NORMAL
324.8167 | 0 | 291.4833 | 0.51403 | 2 | 73773.932 | 14360.5274 | 15786.0725 | 4097.225 | NORMAL
324.8167 | 0 | 291.4833 | 0.51403 | 2 | 90321.356 | 13112.2324 | 14594.3776 | 4097.225 | NORMAL
324.8167 | 0 | 291.4833 | 0.51403 | 2 | 106868.78 | 12226.2357 | 13717.1655 | 4097.225 | NORMAL
324.8167 | 0 | 291.4833 | 0.68163 | 1 | 57226.508 | 10754.5345 | 13763.9191 | 2726.425 | NORMAL
324.8167 | 0 | 291.4833 | 0.68163 | 1 | 73773.932 | 9515.3756 | 12487.9764 | 2726.425 | NORMAL
324.8167 | 0 | 291.4833 | 0.68163 | 1 | 90321.356 | 8688.2475 | 11568.6026 | 2726.425 | NORMAL
324.8167 | 0 | 291.4833 | 0.68163 | 1 | 106868.78 | 8101.1805 | 10868.4294 | 2726.425 | NORMAL
324.8167 | 0 | 291.4833 | 0.68163 | 2 | 57226.508 | 15713.6574 | 18233.3618 | 4168.2025 | NORMAL
324.8167 | 0 | 291.4833 | 0.68163 | 2 | 73773.932 | 13903.0984 | 16506.2518 | 4168.2025 | NORMAL
324.8167 | 0 | 291.4833 | 0.68163 | 2 | 90321.356 | 12694.5656 | 15286.4018 | 4168.2025 | NORMAL
324.8167 | 0 | 291.4833 | 0.68163 | 2 | 106868.78 | 11836.7907 | 14371.6121 | 4168.2025 | NORMAL
324.8167 | 0 | 291.4833 | 0.84923 | 1 | 57226.508 | 10366.6692 | 14226.0623 | 2680.4994 | NORMAL
324.8167 | 0 | 291.4833 | 0.84923 | 1 | 73773.932 | 9172.2008 | 12914.0463 | 2680.4994 | NORMAL
324.8167 | 0 | 291.4833 | 0.84923 | 1 | 90321.356 | 8374.9033 | 11959.4535 | 2680.4994 | NORMAL
324.8167 | 0 | 291.4833 | 0.84923 | 1 | 106868.78 | 7809.0091 | 11226.9201 | 2680.4994 | NORMAL
324.8167 | 0 | 291.4833 | 0.84923 | 2 | 57226.508 | 15180.2976 | 18859.4701 | 4142.8719 | NORMAL
324.8167 | 0 | 291.4833 | 0.84923 | 2 | 73773.932 | 13431.1934 | 17103.7547 | 4142.8719 | NORMAL
324.8167 | 0 | 291.4833 | 0.84923 | 2 | 90321.356 | 12263.6811 | 15845.1045 | 4142.8719 | NORMAL
324.8167 | 0 | 291.4833 | 0.84923 | 2 | 106868.78 | 11435.0213 | 14890.3192 | 4142.8719 | NORMAL
324.8167 | 0 | 296.113 | 0.34644 | 1 | 57226.508 | 10372.8942 | 11807.8445 | 2677.7648 | NORMAL
324.8167 | 0 | 296.113 | 0.34644 | 1 | 73773.932 | 9131.5733 | 10679.4085 | 2677.7648 | NORMAL
324.8167 | 0 | 296.113 | 0.34644 | 1 | 90321.356 | 8327.7276 | 9904.2246 | 2677.7648 | NORMAL
324.8167 | 0 | 296.113 | 0.34644 | 1 | 106868.78 | 7776.3413 | 9337.3221 | 2677.7648 | NORMAL
324.8167 | 0 | 296.113 | 0.34644 | 2 | 57226.508 | 14072.5673 | 14886.2939 | 3607.3926 | NORMAL
324.8167 | 0 | 296.113 | 0.34644 | 2 | 73773.932 | 12388.5076 | 13364.9849 | 3607.3926 | NORMAL
324.8167 | 0 | 296.113 | 0.34644 | 2 | 90321.356 | 11297.9564 | 12354.2226 | 3607.3926 | NORMAL
324.8167 | 0 | 296.113 | 0.34644 | 2 | 106868.78 | 10549.9086 | 11635.1963 | 3607.3926 | NORMAL
324.8167 | 0 | 296.113 | 0.51403 | 1 | 57226.508 | 9947.8546 | 13030.8764 | 2758.5966 | NORMAL
324.8167 | 0 | 296.113 | 0.51403 | 1 | 73773.932 | 8757.398 | 11846.0603 | 2758.5966 | NORMAL
324.8167 | 0 | 296.113 | 0.51403 | 1 | 90321.356 | 7986.4907 | 11001.9506 | 2758.5966 | NORMAL
324.8167 | 0 | 296.113 | 0.51403 | 1 | 106868.78 | 7457.698 | 10366.3118 | 2758.5966 | NORMAL
324.8167 | 0 | 296.113 | 0.51403 | 2 | 57226.508 | 14344.1362 | 16705.763 | 4097.225 | NORMAL
324.8167 | 0 | 296.113 | 0.51403 | 2 | 73773.932 | 12627.578 | 15129.2348 | 4097.225 | NORMAL
324.8167 | 0 | 296.113 | 0.51403 | 2 | 90321.356 | 11515.9816 | 14037.8392 | 4097.225 | NORMAL
324.8167 | 0 | 296.113 | 0.51403 | 2 | 106868.78 | 10753.4981 | 13234.7185 | 4097.225 | NORMAL
324.8167 | 0 | 296.113 | 0.68163 | 1 | 57226.508 | 9504.5147 | 13934.4705 | 2726.425 | NORMAL
324.8167 | 0 | 296.113 | 0.68163 | 1 | 73773.932 | 8367.1124 | 12684.7864 | 2726.425 | NORMAL
324.8167 | 0 | 296.113 | 0.68163 | 1 | 90321.356 | 7630.5617 | 11778.7954 | 2726.425 | NORMAL
324.8167 | 0 | 296.113 | 0.68163 | 1 | 106868.78 | 7125.3353 | 11086.7829 | 2726.425 | NORMAL
324.8167 | 0 | 296.113 | 0.68163 | 2 | 57226.508 | 13887.2293 | 17945.4984 | 4168.2025 | NORMAL
324.8167 | 0 | 296.113 | 0.68163 | 2 | 73773.932 | 12225.349 | 16309.3897 | 4168.2025 | NORMAL
324.8167 | 0 | 296.113 | 0.68163 | 2 | 90321.356 | 11149.1605 | 15146.8222 | 4168.2025 | NORMAL
324.8167 | 0 | 296.113 | 0.68163 | 2 | 106868.78 | 10410.9646 | 14273.2325 | 4168.2025 | NORMAL
324.8167 | 0 | 296.113 | 0.84923 | 1 | 57226.508 | 9161.7317 | 14621.4054 | 2680.4994 | NORMAL
324.8167 | 0 | 296.113 | 0.84923 | 1 | 73773.932 | 8065.3501 | 13315.1258 | 2680.4994 | NORMAL
324.8167 | 0 | 296.113 | 0.84923 | 1 | 90321.356 | 7355.3633 | 12359.0291 | 2680.4994 | NORMAL
324.8167 | 0 | 296.113 | 0.84923 | 1 | 106868.78 | 6868.3581 | 11613.3851 | 2680.4994 | NORMAL
324.8167 | 0 | 296.113 | 0.84923 | 2 | 57226.508 | 13415.863 | 18950.6756 | 4142.8719 | NORMAL
324.8167 | 0 | 296.113 | 0.84923 | 2 | 73773.932 | 11810.3909 | 17245.773 | 4142.8719 | NORMAL
324.8167 | 0 | 296.113 | 0.84923 | 2 | 90321.356 | 10770.7309 | 16015.9656 | 4142.8719 | NORMAL
324.8167 | 0 | 296.113 | 0.84923 | 2 | 106868.78 | 10057.5911 | 15080.4919 | 4142.8719 | NORMAL
324.8167 | 0 | 300.7426 | 0.34644 | 1 | 57226.508 | 9277.3839 | 11612.495 | 2677.7648 | NORMAL
324.8167 | 0 | 300.7426 | 0.34644 | 1 | 73773.932 | 8166.3653 | 10582.9103 | 2677.7648 | NORMAL
324.8167 | 0 | 300.7426 | 0.34644 | 1 | 90321.356 | 7478.9324 | 9874.2989 | 2677.7648 | NORMAL
324.8167 | 0 | 300.7426 | 0.34644 | 1 | 106868.78 | 7033.2753 | 9358.3626 | 2677.7648 | NORMAL
324.8167 | 0 | 300.7426 | 0.34644 | 2 | 57226.508 | 12586.3242 | 14155.1845 | 3607.3926 | NORMAL
324.8167 | 0 | 300.7426 | 0.34644 | 2 | 73773.932 | 11079.0415 | 12826.1097 | 3607.3926 | NORMAL
324.8167 | 0 | 300.7426 | 0.34644 | 2 | 90321.356 | 10146.4237 | 11946.8906 | 3607.3926 | NORMAL
324.8167 | 0 | 300.7426 | 0.34644 | 2 | 106868.78 | 9541.8152 | 11328.1679 | 3607.3926 | NORMAL
324.8167 | 0 | 300.7426 | 0.51403 | 1 | 57226.508 | 8897.2339 | 13301.292 | 2758.5966 | NORMAL
324.8167 | 0 | 300.7426 | 0.51403 | 1 | 73773.932 | 7831.7404 | 12163.2421 | 2758.5966 | NORMAL
324.8167 | 0 | 300.7426 | 0.51403 | 1 | 90321.356 | 7172.4758 | 11349.7438 | 2758.5966 | NORMAL
324.8167 | 0 | 300.7426 | 0.51403 | 1 | 106868.78 | 6745.0799 | 10713.1122 | 2758.5966 | NORMAL
324.8167 | 0 | 300.7426 | 0.51403 | 2 | 57226.508 | 12829.212 | 16555.9635 | 4097.225 | NORMAL
324.8167 | 0 | 300.7426 | 0.51403 | 2 | 73773.932 | 11292.8421 | 15102.0396 | 4097.225 | NORMAL
324.8167 | 0 | 300.7426 | 0.51403 | 2 | 90321.356 | 10342.2269 | 14093.0388 | 4097.225 | NORMAL
324.8167 | 0 | 300.7426 | 0.51403 | 2 | 106868.78 | 9725.9508 | 13353.1404 | 4097.225 | NORMAL
324.8167 | 0 | 300.7426 | 0.68163 | 1 | 57226.508 | 8500.7164 | 14503.8298 | 2726.425 | NORMAL
324.8167 | 0 | 300.7426 | 0.68163 | 1 | 73773.932 | 7482.7081 | 13273.3555 | 2726.425 | NORMAL
324.8167 | 0 | 300.7426 | 0.68163 | 1 | 90321.356 | 6852.8245 | 12343.0547 | 2726.425 | NORMAL
324.8167 | 0 | 300.7426 | 0.68163 | 1 | 106868.78 | 6444.4761 | 11618.8243 | 2726.425 | NORMAL
324.8167 | 0 | 300.7426 | 0.68163 | 2 | 57226.508 | 12420.5603 | 18266.4645 | 4168.2025 | NORMAL
324.8167 | 0 | 300.7426 | 0.68163 | 2 | 73773.932 | 10933.1288 | 16700.8167 | 4168.2025 | NORMAL
324.8167 | 0 | 300.7426 | 0.68163 | 2 | 90321.356 | 10012.7937 | 15584.6325 | 4168.2025 | NORMAL
324.8167 | 0 | 300.7426 | 0.68163 | 2 | 106868.78 | 9416.148 | 14721.0107 | 4168.2025 | NORMAL
324.8167 | 0 | 300.7426 | 0.84923 | 1 | 57226.508 | 8194.1356 | 15394.5292 | 2680.4994 | NORMAL
324.8167 | 0 | 300.7426 | 0.84923 | 1 | 73773.932 | 7212.8421 | 14082.3244 | 2680.4994 | NORMAL
324.8167 | 0 | 300.7426 | 0.84923 | 1 | 90321.356 | 6605.6754 | 13063.2776 | 2680.4994 | NORMAL
324.8167 | 0 | 300.7426 | 0.84923 | 1 | 106868.78 | 6212.0542 | 12281.1591 | 2680.4994 | NORMAL
324.8167 | 0 | 300.7426 | 0.84923 | 2 | 57226.508 | 11998.9763 | 19610.8703 | 4142.8719 | NORMAL
324.8167 | 0 | 300.7426 | 0.84923 | 2 | 73773.932 | 10562.0318 | 17944.0862 | 4142.8719 | NORMAL
324.8167 | 0 | 300.7426 | 0.84923 | 2 | 90321.356 | 9672.9351 | 16709.8378 | 4142.8719 | NORMAL
324.8167 | 0 | 300.7426 | 0.84923 | 2 | 106868.78 | 9096.541 | 15738.7165 | 4142.8719 | NORMAL
324.8167 | 0 | 305.3722 | 0.34644 | 1 | 57226.508 | 8405.8704 | 11782.8158 | 2677.7648 | NORMAL
324.8167 | 0 | 305.3722 | 0.34644 | 1 | 73773.932 | 7440.8893 | 10830.2064 | 2677.7648 | NORMAL
324.8167 | 0 | 305.3722 | 0.34644 | 1 | 90321.356 | 6884.0314 | 10174.9232 | 2677.7648 | NORMAL
324.8167 | 0 | 305.3722 | 0.34644 | 1 | 106868.78 | 6557.011 | 9678.9768 | 2677.7648 | NORMAL
324.8167 | 0 | 305.3722 | 0.34644 | 2 | 57226.508 | 11403.9702 | 13952.4228 | 3607.3926 | NORMAL
324.8167 | 0 | 305.3722 | 0.34644 | 2 | 73773.932 | 10094.8119 | 12779.7554 | 3607.3926 | NORMAL
324.8167 | 0 | 305.3722 | 0.34644 | 2 | 90321.356 | 9339.3409 | 12007.5569 | 3607.3926 | NORMAL
324.8167 | 0 | 305.3722 | 0.34644 | 2 | 106868.78 | 8895.683 | 11472.3191 | 3607.3926 | NORMAL
324.8167 | 0 | 305.3722 | 0.51403 | 1 | 57226.508 | 8061.4315 | 13893.4606 | 2758.5966 | NORMAL
324.8167 | 0 | 305.3722 | 0.51403 | 1 | 73773.932 | 7135.9915 | 12771.2521 | 2758.5966 | NORMAL
324.8167 | 0 | 305.3722 | 0.51403 | 1 | 90321.356 | 6601.9514 | 11930.6807 | 2758.5966 | NORMAL
324.8167 | 0 | 305.3722 | 0.51403 | 1 | 106868.78 | 6288.331 | 11302.8118 | 2758.5966 | NORMAL
324.8167 | 0 | 305.3722 | 0.51403 | 2 | 57226.508 | 11624.0412 | 16902.7304 | 4097.225 | NORMAL
324.8167 | 0 | 305.3722 | 0.51403 | 2 | 73773.932 | 10289.6191 | 15543.9352 | 4097.225 | NORMAL
324.8167 | 0 | 305.3722 | 0.51403 | 2 | 90321.356 | 9519.5692 | 14589.8579 | 4097.225 | NORMAL
324.8167 | 0 | 305.3722 | 0.51403 | 2 | 106868.78 | 9067.3497 | 13863.0084 | 4097.225 | NORMAL
324.8167 | 0 | 305.3722 | 0.68163 | 1 | 57226.508 | 7702.1626 | 15370.7168 | 2726.425 | NORMAL
324.8167 | 0 | 305.3722 | 0.68163 | 1 | 73773.932 | 6817.9662 | 14082.1625 | 2726.425 | NORMAL
324.8167 | 0 | 305.3722 | 0.68163 | 1 | 90321.356 | 6307.7263 | 13135.4314 | 2726.425 | NORMAL
324.8167 | 0 | 305.3722 | 0.68163 | 1 | 106868.78 | 6008.0828 | 12416.4815 | 2726.425 | NORMAL
324.8167 | 0 | 305.3722 | 0.68163 | 2 | 57226.508 | 11253.7781 | 19039.2389 | 4168.2025 | NORMAL
324.8167 | 0 | 305.3722 | 0.68163 | 2 | 73773.932 | 9961.8616 | 17508.5947 | 4168.2025 | NORMAL
324.8167 | 0 | 305.3722 | 0.68163 | 2 | 90321.356 | 9216.3403 | 16359.4219 | 4168.2025 | NORMAL
324.8167 | 0 | 305.3722 | 0.68163 | 2 | 106868.78 | 8778.5254 | 15503.1749 | 4168.2025 | NORMAL
324.8167 | 0 | 305.3722 | 0.84923 | 1 | 57226.508 | 7424.3819 | 16436.0553 | 2680.4994 | NORMAL
324.8167 | 0 | 305.3722 | 0.84923 | 1 | 73773.932 | 6572.0743 | 15037.3754 | 2680.4994 | NORMAL
324.8167 | 0 | 305.3722 | 0.84923 | 1 | 90321.356 | 6080.2363 | 14012.1852 | 2680.4994 | NORMAL
324.8167 | 0 | 305.3722 | 0.84923 | 1 | 106868.78 | 5791.3996 | 13226.4943 | 2680.4994 | NORMAL
324.8167 | 0 | 305.3722 | 0.84923 | 2 | 57226.508 | 10871.7975 | 20694.3813 | 4142.8719 | NORMAL
324.8167 | 0 | 305.3722 | 0.84923 | 2 | 73773.932 | 9623.7318 | 18979.976 | 4142.8719 | NORMAL
324.8167 | 0 | 305.3722 | 0.84923 | 2 | 90321.356 | 8903.5153 | 17712.4363 | 4142.8719 | NORMAL
324.8167 | 0 | 305.3722 | 0.84923 | 2 | 106868.78 | 8480.5609 | 16754.4588 | 4142.8719 | NORMAL
324.8167 | 0.33333 | 291.4833 | 0.34644 | 1 | 57226.508 | 7633.7669 | 6227.7863 | 2677.7648 | NORMAL
324.8167 | 0.33333 | 291.4833 | 0.34644 | 1 | 73773.932 | 7316.7406 | 6222.1612 | 2677.7648 | NORMAL
324.8167 | 0.33333 | 291.4833 | 0.34644 | 1 | 90321.356 | 7087.7904 | 6203.5558 | 2677.7648 | NORMAL
324.8167 | 0.33333 | 291.4833 | 0.34644 | 1 | 106868.78 | 6917.0185 | 6181.6494 | 2677.7648 | NORMAL
324.8167 | 0.33333 | 291.4833 | 0.34644 | 2 | 57226.508 | 10356.4826 | 7698.8614 | 3607.3926 | NORMAL
324.8167 | 0.33333 | 291.4833 | 0.34644 | 2 | 73773.932 | 9926.3834 | 7792.189 | 3607.3926 | NORMAL
324.8167 | 0.33333 | 291.4833 | 0.34644 | 2 | 90321.356 | 9615.7741 | 7841.7711 | 3607.3926 | NORMAL
324.8167 | 0.33333 | 291.4833 | 0.34644 | 2 | 106868.78 | 9384.0934 | 7870.2213 | 3607.3926 | NORMAL
324.8167 | 0.33333 | 291.4833 | 0.51403 | 1 | 57226.508 | 7320.9658 | 6954.482 | 2758.5966 | NORMAL
324.8167 | 0.33333 | 291.4833 | 0.51403 | 1 | 73773.932 | 7016.9299 | 6836.4016 | 2758.5966 | NORMAL
324.8167 | 0.33333 | 291.4833 | 0.51403 | 1 | 90321.356 | 6797.3612 | 6730.6541 | 2758.5966 | NORMAL
324.8167 | 0.33333 | 291.4833 | 0.51403 | 1 | 106868.78 | 6633.5868 | 6638.8607 | 2758.5966 | NORMAL
324.8167 | 0.33333 | 291.4833 | 0.51403 | 2 | 57226.508 | 10556.3395 | 8846.3889 | 4097.225 | NORMAL
324.8167 | 0.33333 | 291.4833 | 0.51403 | 2 | 73773.932 | 10117.9403 | 8811.1067 | 4097.225 | NORMAL
324.8167 | 0.33333 | 291.4833 | 0.51403 | 2 | 90321.356 | 9801.337 | 8764.2837 | 4097.225 | NORMAL
324.8167 | 0.33333 | 291.4833 | 0.51403 | 2 | 106868.78 | 9565.1853 | 8717.1446 | 4097.225 | NORMAL
324.8167 | 0.33333 | 291.4833 | 0.68163 | 1 | 57226.508 | 6994.6968 | 7433.2091 | 2726.425 | NORMAL
324.8167 | 0.33333 | 291.4833 | 0.68163 | 1 | 73773.932 | 6704.2107 | 7238.2258 | 2726.425 | NORMAL
324.8167 | 0.33333 | 291.4833 | 0.68163 | 1 | 90321.356 | 6494.4274 | 7072.4064 | 2726.425 | NORMAL
324.8167 | 0.33333 | 291.4833 | 0.68163 | 1 | 106868.78 | 6337.9518 | 6931.8688 | 2726.425 | NORMAL
324.8167 | 0.33333 | 291.4833 | 0.68163 | 2 | 57226.508 | 10220.0861 | 9575.7532 | 4168.2025 | NORMAL
324.8167 | 0.33333 | 291.4833 | 0.68163 | 2 | 73773.932 | 9795.6513 | 9425.2653 | 4168.2025 | NORMAL
324.8167 | 0.33333 | 291.4833 | 0.68163 | 2 | 90321.356 | 9489.1329 | 9288.8748 | 4168.2025 | NORMAL
324.8167 | 0.33333 | 291.4833 | 0.68163 | 2 | 106868.78 | 9260.5034 | 9169.8396 | 4168.2025 | NORMAL
324.8167 | 0.33333 | 291.4833 | 0.84923 | 1 | 57226.508 | 6742.431 | 7786.4123 | 2680.4994 | NORMAL
324.8167 | 0.33333 | 291.4833 | 0.84923 | 1 | 73773.932 | 6462.4215 | 7536.3761 | 2680.4994 | NORMAL
324.8167 | 0.33333 | 291.4833 | 0.84923 | 1 | 90321.356 | 6260.204 | 7327.2052 | 2680.4994 | NORMAL
324.8167 | 0.33333 | 291.4833 | 0.84923 | 1 | 106868.78 | 6109.3718 | 7151.2588 | 2680.4994 | NORMAL
324.8167 | 0.33333 | 291.4833 | 0.84923 | 2 | 57226.508 | 9873.1915 | 10113.6072 | 4142.8719 | NORMAL
324.8167 | 0.33333 | 291.4833 | 0.84923 | 2 | 73773.932 | 9463.1631 | 9877.0896 | 4142.8719 | NORMAL
324.8167 | 0.33333 | 291.4833 | 0.84923 | 2 | 90321.356 | 9167.0486 | 9673.6605 | 4142.8719 | NORMAL
324.8167 | 0.33333 | 291.4833 | 0.84923 | 2 | 106868.78 | 8946.1794 | 9500.3385 | 4142.8719 | NORMAL
324.8167 | 0.33333 | 296.113 | 0.34644 | 1 | 57226.508 | 6648.2783 | 5839.8283 | 2677.7648 | NORMAL
324.8167 | 0.33333 | 296.113 | 0.34644 | 1 | 73773.932 | 6486.0408 | 5837.4912 | 2677.7648 | NORMAL
324.8167 | 0.33333 | 296.113 | 0.34644 | 1 | 90321.356 | 6381.1172 | 5838.2488 | 2677.7648 | NORMAL
324.8167 | 0.33333 | 296.113 | 0.34644 | 1 | 106868.78 | 6313.4844 | 5843.2453 | 2677.7648 | NORMAL
324.8167 | 0.33333 | 296.113 | 0.34644 | 2 | 57226.508 | 9019.5024 | 6998.6401 | 3607.3926 | NORMAL
324.8167 | 0.33333 | 296.113 | 0.34644 | 2 | 73773.932 | 8799.4001 | 7102.0091 | 3607.3926 | NORMAL
324.8167 | 0.33333 | 296.113 | 0.34644 | 2 | 90321.356 | 8657.0536 | 7187.9054 | 3607.3926 | NORMAL
324.8167 | 0.33333 | 296.113 | 0.34644 | 2 | 106868.78 | 8565.2984 | 7264.2614 | 3607.3926 | NORMAL
324.8167 | 0.33333 | 296.113 | 0.51403 | 1 | 57226.508 | 6375.8586 | 6754.2062 | 2758.5966 | NORMAL
324.8167 | 0.33333 | 296.113 | 0.51403 | 1 | 73773.932 | 6220.2689 | 6638.349 | 2758.5966 | NORMAL
324.8167 | 0.33333 | 296.113 | 0.51403 | 1 | 90321.356 | 6119.6446 | 6547.1828 | 2758.5966 | NORMAL
324.8167 | 0.33333 | 296.113 | 0.51403 | 1 | 106868.78 | 6054.7831 | 6475.499 | 2758.5966 | NORMAL
324.8167 | 0.33333 | 296.113 | 0.51403 | 2 | 57226.508 | 9193.5586 | 8348.4273 | 4097.225 | NORMAL
324.8167 | 0.33333 | 296.113 | 0.51403 | 2 | 73773.932 | 8969.2088 | 8316.6788 | 4097.225 | NORMAL
324.8167 | 0.33333 | 296.113 | 0.51403 | 2 | 90321.356 | 8824.1153 | 8294.7744 | 4097.225 | NORMAL
324.8167 | 0.33333 | 296.113 | 0.51403 | 2 | 106868.78 | 8730.5894 | 8282.6752 | 4097.225 | NORMAL
324.8167 | 0.33333 | 296.113 | 0.68163 | 1 | 57226.508 | 6091.7096 | 7377.8808 | 2726.425 | NORMAL
324.8167 | 0.33333 | 296.113 | 0.68163 | 1 | 73773.932 | 5943.054 | 7183.3083 | 2726.425 | NORMAL
324.8167 | 0.33333 | 296.113 | 0.68163 | 1 | 90321.356 | 5846.9141 | 7027.9653 | 2726.425 | NORMAL
324.8167 | 0.33333 | 296.113 | 0.68163 | 1 | 106868.78 | 5784.9433 | 6902.3516 | 2726.425 | NORMAL
324.8167 | 0.33333 | 296.113 | 0.68163 | 2 | 57226.508 | 8900.7141 | 9271.3893 | 4168.2025 | NORMAL
324.8167 | 0.33333 | 296.113 | 0.68163 | 2 | 73773.932 | 8683.5106 | 9124.3833 | 4168.2025 | NORMAL
324.8167 | 0.33333 | 296.113 | 0.68163 | 2 | 90321.356 | 8543.0388 | 9009.0769 | 4168.2025 | NORMAL
324.8167 | 0.33333 | 296.113 | 0.68163 | 2 | 106868.78 | 8452.492 | 8919.0005 | 4168.2025 | NORMAL
324.8167 | 0.33333 | 296.113 | 0.84923 | 1 | 57226.508 | 5872.0103 | 7831.0967 | 2680.4994 | NORMAL
324.8167 | 0.33333 | 296.113 | 0.84923 | 1 | 73773.932 | 5728.7161 | 7580.4814 | 2680.4994 | NORMAL
324.8167 | 0.33333 | 296.113 | 0.84923 | 1 | 90321.356 | 5636.0435 | 7379.3421 | 2680.4994 | NORMAL
324.8167 | 0.33333 | 296.113 | 0.84923 | 1 | 106868.78 | 5576.3077 | 7215.1514 | 2680.4994 | NORMAL
324.8167 | 0.33333 | 296.113 | 0.84923 | 2 | 57226.508 | 8598.6022 | 9972.8016 | 4142.8719 | NORMAL
324.8167 | 0.33333 | 296.113 | 0.84923 | 2 | 73773.932 | 8388.7711 | 9737.5721 | 4142.8719 | NORMAL
324.8167 | 0.33333 | 296.113 | 0.84923 | 2 | 90321.356 | 8253.0673 | 9550.3962 | 4142.8719 | NORMAL
324.8167 | 0.33333 | 296.113 | 0.84923 | 2 | 106868.78 | 8165.5939 | 9399.9808 | 4142.8719 | NORMAL
324.8167 | 0.33333 | 300.7426 | 0.34644 | 1 | 57226.508 | 6240.731 | 5791.2877 | 2644.7798 | NORMAL
324.8167 | 0.33333 | 300.7426 | 0.34644 | 1 | 73773.932 | 6230.5046 | 5805.495 | 2625.9423 | NORMAL
324.8167 | 0.33333 | 300.7426 | 0.34644 | 1 | 90321.356 | 6251.0131 | 5835.7153 | 2616.4549 | NORMAL
324.8167 | 0.33333 | 300.7426 | 0.34644 | 1 | 106868.78 | 6290.2974 | 5876.6583 | 2612.8352 | NORMAL
324.8167 | 0.33333 | 300.7426 | 0.34644 | 2 | 57226.508 | 8466.5963 | 6767.3759 | 3562.9564 | NORMAL
324.8167 | 0.33333 | 300.7426 | 0.34644 | 2 | 73773.932 | 8452.7224 | 6895.1657 | 3537.5792 | NORMAL
324.8167 | 0.33333 | 300.7426 | 0.34644 | 2 | 90321.356 | 8480.5456 | 7027.2081 | 3524.7981 | NORMAL
324.8167 | 0.33333 | 300.7426 | 0.34644 | 2 | 106868.78 | 8533.8413 | 7160.8208 | 3519.9217 | NORMAL
324.8167 | 0.33333 | 300.7426 | 0.51403 | 1 | 57226.508 | 5985.0109 | 6875.9307 | 2724.616 | NORMAL
324.8167 | 0.33333 | 300.7426 | 0.51403 | 1 | 73773.932 | 5975.2035 | 6775.1807 | 2705.2098 | NORMAL
324.8167 | 0.33333 | 300.7426 | 0.51403 | 1 | 90321.356 | 5994.8716 | 6708.6633 | 2695.436 | NORMAL
324.8167 | 0.33333 | 300.7426 | 0.51403 | 1 | 106868.78 | 6032.5462 | 6666.1127 | 2691.7071 | NORMAL
324.8167 | 0.33333 | 300.7426 | 0.51403 | 2 | 57226.508 | 8629.9826 | 8324.2611 | 4046.755 | NORMAL
324.8167 | 0.33333 | 300.7426 | 0.51403 | 2 | 73773.932 | 8615.841 | 8315.0972 | 4017.9319 | NORMAL
324.8167 | 0.33333 | 300.7426 | 0.51403 | 2 | 90321.356 | 8644.2011 | 8332.775 | 4003.4153 | NORMAL
324.8167 | 0.33333 | 300.7426 | 0.51403 | 2 | 106868.78 | 8698.5253 | 8368.7154 | 3997.8768 | NORMAL
324.8167 | 0.33333 | 300.7426 | 0.68163 | 1 | 57226.508 | 5718.2806 | 7615.5598 | 2692.8406 | NORMAL
324.8167 | 0.33333 | 300.7426 | 0.68163 | 1 | 73773.932 | 5708.9103 | 7435.2131 | 2673.6608 | NORMAL
324.8167 | 0.33333 | 300.7426 | 0.68163 | 1 | 90321.356 | 5727.7019 | 7301.7287 | 2664.001 | NORMAL
324.8167 | 0.33333 | 300.7426 | 0.68163 | 1 | 106868.78 | 5763.6974 | 7201.2939 | 2660.3155 | NORMAL
324.8167 | 0.33333 | 300.7426 | 0.68163 | 2 | 57226.508 | 8355.0899 | 9419.822 | 4116.8582 | NORMAL
324.8167 | 0.33333 | 300.7426 | 0.68163 | 2 | 73773.932 | 8341.3987 | 9293.9616 | 4087.5358 | NORMAL
324.8167 | 0.33333 | 300.7426 | 0.68163 | 2 | 90321.356 | 8368.8555 | 9213.4209 | 4072.7677 | NORMAL
324.8167 | 0.33333 | 300.7426 | 0.68163 | 2 | 106868.78 | 8421.4493 | 9164.5607 | 4067.1333 | NORMAL
324.8167 | 0.33333 | 300.7426 | 0.84923 | 1 | 57226.508 | 5512.0492 | 8150.6295 | 2647.4808 | NORMAL
324.8167 | 0.33333 | 300.7426 | 0.84923 | 1 | 73773.932 | 5503.0168 | 7913.6513 | 2628.624 | NORMAL
324.8167 | 0.33333 | 300.7426 | 0.84923 | 1 | 90321.356 | 5521.1307 | 7732.5772 | 2619.1269 | NORMAL
324.8167 | 0.33333 | 300.7426 | 0.84923 | 1 | 106868.78 | 5555.828 | 7591.0275 | 2615.5035 | NORMAL
324.8167 | 0.33333 | 300.7426 | 0.84923 | 2 | 57226.508 | 8071.4978 | 10251.4941 | 4091.8396 | NORMAL
324.8167 | 0.33333 | 300.7426 | 0.84923 | 2 | 73773.932 | 8058.2714 | 10036.4178 | 4062.6953 | NORMAL
324.8167 | 0.33333 | 300.7426 | 0.84923 | 2 | 90321.356 | 8084.7961 | 9880.813 | 4048.017 | NORMAL
324.8167 | 0.33333 | 300.7426 | 0.84923 | 2 | 106868.78 | 8135.6048 | 9767.08 | 4042.4169 | NORMAL
324.8167 | 0.33333 | 305.3722 | 0.34644 | 1 | 57226.508 | 6423.7723 | 5980.2849 | 2616.8305 | NORMAL
324.8167 | 0.33333 | 305.3722 | 0.34644 | 1 | 73773.932 | 6555.5533 | 6022.6607 | 2626.518 | NORMAL
324.8167 | 0.33333 | 305.3722 | 0.34644 | 1 | 90321.356 | 6696.528 | 6091.931 | 2638.4328 | NORMAL
324.8167 | 0.33333 | 305.3722 | 0.34644 | 1 | 106868.78 | 6840.7936 | 6177.9161 | 2650.8845 | NORMAL
324.8167 | 0.33333 | 305.3722 | 0.34644 | 2 | 57226.508 | 8714.9224 | 6885.3965 | 3525.304 | NORMAL
324.8167 | 0.33333 | 305.3722 | 0.34644 | 2 | 73773.932 | 8893.7053 | 7053.2461 | 3538.3546 | NORMAL
324.8167 | 0.33333 | 305.3722 | 0.34644 | 2 | 90321.356 | 9084.9611 | 7243.4058 | 3554.4059 | NORMAL
324.8167 | 0.33333 | 305.3722 | 0.34644 | 2 | 106868.78 | 9280.6816 | 7445.6982 | 3571.1804 | NORMAL
324.8167 | 0.33333 | 305.3722 | 0.51403 | 1 | 57226.508 | 6160.5519 | 7209.3046 | 2695.8229 | NORMAL
324.8167 | 0.33333 | 305.3722 | 0.51403 | 1 | 73773.932 | 6286.933 | 7134.7502 | 2705.8028 | NORMAL
324.8167 | 0.33333 | 305.3722 | 0.51403 | 1 | 90321.356 | 6422.1311 | 7102.7788 | 2718.0774 | NORMAL
324.8167 | 0.33333 | 305.3722 | 0.51403 | 1 | 106868.78 | 6560.4853 | 7098.8778 | 2730.9049 | NORMAL
324.8167 | 0.33333 | 305.3722 | 0.51403 | 2 | 57226.508 | 8883.1009 | 8623.3079 | 4003.9899 | NORMAL
324.8167 | 0.33333 | 305.3722 | 0.51403 | 2 | 73773.932 | 9065.3339 | 8652.7891 | 4018.8126 | NORMAL
324.8167 | 0.33333 | 305.3722 | 0.51403 | 2 | 90321.356 | 9260.2804 | 8723.5059 | 4037.0435 | NORMAL
324.8167 | 0.33333 | 305.3722 | 0.51403 | 2 | 106868.78 | 9459.7779 | 8820.2704 | 4056.0957 | NORMAL
324.8167 | 0.33333 | 305.3722 | 0.68163 | 1 | 57226.508 | 5885.9984 | 8048.6293 | 2664.3833 | NORMAL
324.8167 | 0.33333 | 305.3722 | 0.68163 | 1 | 73773.932 | 6006.7471 | 7893.1138 | 2674.2469 | NORMAL
324.8167 | 0.33333 | 305.3722 | 0.68163 | 1 | 90321.356 | 6135.9199 | 7791.4241 | 2686.3782 | NORMAL
324.8167 | 0.33333 | 305.3722 | 0.68163 | 1 | 106868.78 | 6268.1082 | 7725.8528 | 2699.0562 | NORMAL
324.8167 | 0.33333 | 305.3722 | 0.68163 | 2 | 57226.508 | 8600.1455 | 9865.2505 | 4073.3522 | NORMAL
324.8167 | 0.33333 | 305.3722 | 0.68163 | 2 | 73773.932 | 8776.5738 | 9776.0196 | 4088.4318 | NORMAL
324.8167 | 0.33333 | 305.3722 | 0.68163 | 2 | 90321.356 | 8965.3107 | 9743.9768 | 4106.9784 | NORMAL
324.8167 | 0.33333 | 305.3722 | 0.68163 | 2 | 106868.78 | 9158.4535 | 9749.5159 | 4126.3607 | NORMAL
324.8167 | 0.33333 | 305.3722 | 0.84923 | 1 | 57226.508 | 5673.7182 | 8654.9863 | 2619.5028 | NORMAL
324.8167 | 0.33333 | 305.3722 | 0.84923 | 1 | 73773.932 | 5790.1121 | 8441.916 | 2629.2002 | NORMAL
324.8167 | 0.33333 | 305.3722 | 0.84923 | 1 | 90321.356 | 5914.6262 | 8290.8555 | 2641.1273 | NORMAL
324.8167 | 0.33333 | 305.3722 | 0.84923 | 1 | 106868.78 | 6042.0471 | 8181.7453 | 2653.5917 | NORMAL
324.8167 | 0.33333 | 305.3722 | 0.84923 | 2 | 57226.508 | 8308.2357 | 10808.7368 | 4048.598 | NORMAL
324.8167 | 0.33333 | 305.3722 | 0.84923 | 2 | 73773.932 | 8478.6756 | 10628.7685 | 4063.5859 | NORMAL
324.8167 | 0.33333 | 305.3722 | 0.84923 | 2 | 90321.356 | 8661.0062 | 10518.5328 | 4082.0199 | NORMAL
324.8167 | 0.33333 | 305.3722 | 0.84923 | 2 | 106868.78 | 8847.5933 | 10454.8698 | 4101.2844 | NORMAL
324.8167 | 0.66667 | 291.4833 | 0.34644 | 1 | 57226.508 | 6312.3723 | 3307.2525 | 2677.7648 | NORMAL
324.8167 | 0.66667 | 291.4833 | 0.34644 | 1 | 73773.932 | 6285.1059 | 3560.9 | 2670.6255 | NORMAL
324.8167 | 0.66667 | 291.4833 | 0.34644 | 1 | 90321.356 | 6266.0937 | 3780.4164 | 2660.8981 | NORMAL
324.8167 | 0.66667 | 291.4833 | 0.34644 | 1 | 106868.78 | 6252.7596 | 3970.1288 | 2653.16 | NORMAL
324.8167 | 0.66667 | 291.4833 | 0.34644 | 2 | 57226.508 | 8563.7897 | 4155.7275 | 3607.3926 | NORMAL
324.8167 | 0.66667 | 291.4833 | 0.34644 | 2 | 73773.932 | 8526.7982 | 4561.7564 | 3597.7748 | NORMAL
324.8167 | 0.66667 | 291.4833 | 0.34644 | 2 | 90321.356 | 8501.005 | 4910.4525 | 3584.6704 | NORMAL
324.8167 | 0.66667 | 291.4833 | 0.34644 | 2 | 106868.78 | 8482.9151 | 5209.3695 | 3574.246 | NORMAL
324.8167 | 0.66667 | 291.4833 | 0.51403 | 1 | 57226.508 | 6053.7166 | 3609.1915 | 2758.5966 | NORMAL
324.8167 | 0.66667 | 291.4833 | 0.51403 | 1 | 73773.932 | 6027.5674 | 3795.8505 | 2751.2418 | NORMAL
324.8167 | 0.66667 | 291.4833 | 0.51403 | 1 | 90321.356 | 6009.3343 | 3959.3098 | 2741.2208 | NORMAL
324.8167 | 0.66667 | 291.4833 | 0.51403 | 1 | 106868.78 | 5996.5466 | 4101.7845 | 2733.2492 | NORMAL
324.8167 | 0.66667 | 291.4833 | 0.51403 | 2 | 57226.508 | 8729.0516 | 4674.8576 | 4097.225 | NORMAL
324.8167 | 0.66667 | 291.4833 | 0.51403 | 2 | 73773.932 | 8691.3462 | 5010.4953 | 4086.3012 | NORMAL
324.8167 | 0.66667 | 291.4833 | 0.51403 | 2 | 90321.356 | 8665.0553 | 5301.5197 | 4071.4175 | NORMAL
324.8167 | 0.66667 | 291.4833 | 0.51403 | 2 | 106868.78 | 8646.6163 | 5553.4463 | 4059.5775 | NORMAL
324.8167 | 0.66667 | 291.4833 | 0.68163 | 1 | 57226.508 | 5783.9243 | 3807.7724 | 2726.425 | NORMAL
324.8167 | 0.66667 | 291.4833 | 0.68163 | 1 | 73773.932 | 5758.9405 | 3948.2323 | 2719.1559 | NORMAL
324.8167 | 0.66667 | 291.4833 | 0.68163 | 1 | 90321.356 | 5741.52 | 4072.823 | 2709.2518 | NORMAL
324.8167 | 0.66667 | 291.4833 | 0.68163 | 1 | 106868.78 | 5729.3022 | 4182.1522 | 2701.3731 | NORMAL
324.8167 | 0.66667 | 291.4833 | 0.68163 | 2 | 57226.508 | 8451.0032 | 4977.7627 | 4168.2025 | NORMAL
324.8167 | 0.66667 | 291.4833 | 0.68163 | 2 | 73773.932 | 8414.4989 | 5245.2499 | 4157.0895 | NORMAL
324.8167 | 0.66667 | 291.4833 | 0.68163 | 2 | 90321.356 | 8389.0454 | 5479.199 | 4141.9479 | NORMAL
324.8167 | 0.66667 | 291.4833 | 0.68163 | 2 | 106868.78 | 8371.1938 | 5682.9617 | 4129.9028 | NORMAL
324.8167 | 0.66667 | 291.4833 | 0.84923 | 1 | 57226.508 | 5575.3255 | 3952.7185 | 2680.4994 | NORMAL
324.8167 | 0.66667 | 291.4833 | 0.84923 | 1 | 73773.932 | 5551.2427 | 4060.8927 | 2673.3528 | NORMAL
324.8167 | 0.66667 | 291.4833 | 0.84923 | 1 | 90321.356 | 5534.4504 | 4158.2956 | 2663.6155 | NORMAL
324.8167 | 0.66667 | 291.4833 | 0.84923 | 1 | 106868.78 | 5522.6733 | 4244.3514 | 2655.8695 | NORMAL
324.8167 | 0.66667 | 291.4833 | 0.84923 | 2 | 57226.508 | 8164.1556 | 5202.4961 | 4142.8719 | NORMAL
324.8167 | 0.66667 | 291.4833 | 0.84923 | 2 | 73773.932 | 8128.8903 | 5418.2045 | 4131.8264 | NORMAL
324.8167 | 0.66667 | 291.4833 | 0.84923 | 2 | 90321.356 | 8104.3008 | 5608.6148 | 4116.7768 | NORMAL
324.8167 | 0.66667 | 291.4833 | 0.84923 | 2 | 106868.78 | 8087.0551 | 5775.3012 | 4104.8049 | NORMAL
324.8167 | 0.66667 | 296.113 | 0.34644 | 1 | 57226.508 | 6367.1926 | 3142.7926 | 2613.834 | NORMAL
324.8167 | 0.66667 | 296.113 | 0.34644 | 1 | 73773.932 | 6405.7703 | 3382.4109 | 2615.7591 | NORMAL
324.8167 | 0.66667 | 296.113 | 0.34644 | 1 | 90321.356 | 6443.4741 | 3604.7929 | 2618.0983 | NORMAL
324.8167 | 0.66667 | 296.113 | 0.34644 | 1 | 106868.78 | 6479.8867 | 3809.1658 | 2620.6473 | NORMAL
324.8167 | 0.66667 | 296.113 | 0.34644 | 2 | 57226.508 | 8638.1626 | 3856.5554 | 3521.2673 | NORMAL
324.8167 | 0.66667 | 296.113 | 0.34644 | 2 | 73773.932 | 8690.4996 | 4240.5095 | 3523.8607 | NORMAL
324.8167 | 0.66667 | 296.113 | 0.34644 | 2 | 90321.356 | 8741.6512 | 4594.4306 | 3527.012 | NORMAL
324.8167 | 0.66667 | 296.113 | 0.34644 | 2 | 106868.78 | 8791.051 | 4917.6441 | 3530.4459 | NORMAL
324.8167 | 0.66667 | 296.113 | 0.51403 | 1 | 57226.508 | 6106.2906 | 3524.9566 | 2692.736 | NORMAL
324.8167 | 0.66667 | 296.113 | 0.51403 | 1 | 73773.932 | 6143.2875 | 3700.5107 | 2694.7193 | NORMAL
324.8167 | 0.66667 | 296.113 | 0.51403 | 1 | 90321.356 | 6179.4464 | 3866.453 | 2697.129 | NORMAL
324.8167 | 0.66667 | 296.113 | 0.51403 | 1 | 106868.78 | 6214.3669 | 4020.8584 | 2699.755 | NORMAL
324.8167 | 0.66667 | 296.113 | 0.51403 | 2 | 57226.508 | 8804.8598 | 4466.594 | 3999.4051 | NORMAL
324.8167 | 0.66667 | 296.113 | 0.51403 | 2 | 73773.932 | 8858.2067 | 4783.5206 | 4002.3507 | NORMAL
324.8167 | 0.66667 | 296.113 | 0.51403 | 2 | 90321.356 | 8910.3454 | 5078.3561 | 4005.9298 | NORMAL
324.8167 | 0.66667 | 296.113 | 0.51403 | 2 | 106868.78 | 8960.6985 | 5349.8057 | 4009.83 | NORMAL
324.8167 | 0.66667 | 296.113 | 0.68163 | 1 | 57226.508 | 5834.1553 | 3778.5639 | 2661.3325 | NORMAL
324.8167 | 0.66667 | 296.113 | 0.68163 | 1 | 73773.932 | 5869.5034 | 3909.6848 | 2663.2925 | NORMAL
324.8167 | 0.66667 | 296.113 | 0.68163 | 1 | 90321.356 | 5904.0508 | 4036.7229 | 2665.6742 | NORMAL
324.8167 | 0.66667 | 296.113 | 0.68163 | 1 | 106868.78 | 5937.4151 | 4156.6818 | 2668.2695 | NORMAL
324.8167 | 0.66667 | 296.113 | 0.68163 | 2 | 57226.508 | 8524.3966 | 4850.9721 | 4068.688 | NORMAL
324.8167 | 0.66667 | 296.113 | 0.68163 | 2 | 73773.932 | 8576.0443 | 5102.7013 | 4071.6846 | NORMAL
324.8167 | 0.66667 | 296.113 | 0.68163 | 2 | 90321.356 | 8626.5223 | 5340.1173 | 4075.3258 | NORMAL
324.8167 | 0.66667 | 296.113 | 0.68163 | 2 | 106868.78 | 8675.2714 | 5560.7181 | 4079.2935 | NORMAL
324.8167 | 0.66667 | 296.113 | 0.84923 | 1 | 57226.508 | 5623.7448 | 3962.1776 | 2616.5034 | NORMAL
324.8167 | 0.66667 | 296.113 | 0.84923 | 1 | 73773.932 | 5657.8181 | 4062.1419 | 2618.4304 | NORMAL
324.8167 | 0.66667 | 296.113 | 0.84923 | 1 | 90321.356 | 5691.1195 | 4162.0121 | 2620.772 | NORMAL
324.8167 | 0.66667 | 296.113 | 0.84923 | 1 | 106868.78 | 5723.2805 | 4257.9466 | 2623.3236 | NORMAL
324.8167 | 0.66667 | 296.113 | 0.84923 | 2 | 57226.508 | 8235.0579 | 5137.4389 | 4043.9621 | NORMAL
324.8167 | 0.66667 | 296.113 | 0.84923 | 2 | 73773.932 | 8284.9525 | 5339.413 | 4046.9405 | NORMAL
324.8167 | 0.66667 | 296.113 | 0.84923 | 2 | 90321.356 | 8333.7171 | 5533.226 | 4050.5595 | NORMAL
324.8167 | 0.66667 | 296.113 | 0.84923 | 2 | 106868.78 | 8380.8116 | 5715.2159 | 4054.5032 | NORMAL
324.8167 | 0.66667 | 300.7426 | 0.34644 | 1 | 57226.508 | 7296.7095 | 3214.3164 | 2686.4326 | NORMAL
324.8167 | 0.66667 | 300.7426 | 0.34644 | 1 | 73773.932 | 7391.7608 | 3474.7396 | 2689.0862 | NORMAL
324.8167 | 0.66667 | 300.7426 | 0.34644 | 1 | 90321.356 | 7479.7518 | 3729.6557 | 2689.0862 | NORMAL
324.8167 | 0.66667 | 300.7426 | 0.34644 | 1 | 106868.78 | 7561.8996 | 3973.9295 | 2689.0862 | NORMAL
324.8167 | 0.66667 | 300.7426 | 0.34644 | 2 | 57226.508 | 9899.2079 | 3899.0164 | 3619.0697 | NORMAL
324.8167 | 0.66667 | 300.7426 | 0.34644 | 2 | 73773.932 | 10028.1608 | 4313.5434 | 3622.6444 | NORMAL
324.8167 | 0.66667 | 300.7426 | 0.34644 | 2 | 90321.356 | 10147.5354 | 4716.6987 | 3622.6444 | NORMAL
324.8167 | 0.66667 | 300.7426 | 0.34644 | 2 | 106868.78 | 10258.9826 | 5101.5962 | 3622.6444 | NORMAL
324.8167 | 0.66667 | 300.7426 | 0.51403 | 1 | 57226.508 | 6997.7197 | 3653.9513 | 2767.5261 | NORMAL
324.8167 | 0.66667 | 300.7426 | 0.51403 | 1 | 73773.932 | 7088.8761 | 3848.2859 | 2770.2598 | NORMAL
324.8167 | 0.66667 | 300.7426 | 0.51403 | 1 | 90321.356 | 7173.2616 | 4042.8288 | 2770.2598 | NORMAL
324.8167 | 0.66667 | 300.7426 | 0.51403 | 1 | 106868.78 | 7252.0433 | 4231.413 | 2770.2598 | NORMAL
324.8167 | 0.66667 | 300.7426 | 0.51403 | 2 | 57226.508 | 10090.2404 | 4580.4328 | 4110.4876 | NORMAL
324.8167 | 0.66667 | 300.7426 | 0.51403 | 2 | 73773.932 | 10221.6818 | 4925.7168 | 4114.5477 | NORMAL
324.8167 | 0.66667 | 300.7426 | 0.51403 | 2 | 90321.356 | 10343.36 | 5264.6353 | 4114.5477 | NORMAL
324.8167 | 0.66667 | 300.7426 | 0.51403 | 2 | 106868.78 | 10456.9579 | 5589.8783 | 4114.5477 | NORMAL
324.8167 | 0.66667 | 300.7426 | 0.68163 | 1 | 57226.508 | 6685.8566 | 3947.4206 | 2735.2503 | NORMAL
324.8167 | 0.66667 | 300.7426 | 0.68163 | 1 | 73773.932 | 6772.9505 | 4096.0898 | 2737.9521 | NORMAL
324.8167 | 0.66667 | 300.7426 | 0.68163 | 1 | 90321.356 | 6853.5752 | 4249.545 | 2737.9521 | NORMAL
324.8167 | 0.66667 | 300.7426 | 0.68163 | 1 | 106868.78 | 6928.8459 | 4400.5688 | 2737.9521 | NORMAL
324.8167 | 0.66667 | 300.7426 | 0.68163 | 2 | 57226.508 | 9768.8337 | 5023.1081 | 4181.6949 | NORMAL
324.8167 | 0.66667 | 300.7426 | 0.68163 | 2 | 73773.932 | 9896.0883 | 5301.1538 | 4185.8253 | NORMAL
324.8167 | 0.66667 | 300.7426 | 0.68163 | 2 | 90321.356 | 10013.8907 | 5578.7193 | 4185.8253 | NORMAL
324.8167 | 0.66667 | 300.7426 | 0.68163 | 2 | 106868.78 | 10123.8702 | 5847.4028 | 4185.8253 | NORMAL
324.8167 | 0.66667 | 300.7426 | 0.84923 | 1 | 57226.508 | 6444.7293 | 4159.5786 | 2689.1761 | NORMAL
324.8167 | 0.66667 | 300.7426 | 0.84923 | 1 | 73773.932 | 6528.6821 | 4276.2983 | 2691.8323 | NORMAL
324.8167 | 0.66667 | 300.7426 | 0.84923 | 1 | 90321.356 | 6606.3991 | 4401.2454 | 2691.8323 | NORMAL
324.8167 | 0.66667 | 300.7426 | 0.84923 | 1 | 106868.78 | 6678.9551 | 4526.3469 | 2691.8323 | NORMAL
324.8167 | 0.66667 | 300.7426 | 0.84923 | 2 | 57226.508 | 9437.2558 | 5354.2559 | 4156.2822 | NORMAL
324.8167 | 0.66667 | 300.7426 | 0.84923 | 2 | 73773.932 | 9560.191 | 5581.1461 | 4160.3876 | NORMAL
324.8167 | 0.66667 | 300.7426 | 0.84923 | 2 | 90321.356 | 9673.9949 | 5812.5894 | 4160.3876 | NORMAL
324.8167 | 0.66667 | 300.7426 | 0.84923 | 2 | 106868.78 | 9780.2414 | 6039.0553 | 4160.3876 | NORMAL
324.8167 | 0.66667 | 305.3722 | 0.34644 | 1 | 57226.508 | 9113.8562 | 3414.2725 | 2689.0862 | NORMAL
324.8167 | 0.66667 | 305.3722 | 0.34644 | 1 | 73773.932 | 9254.5161 | 3718.4759 | 2689.0862 | NORMAL
324.8167 | 0.66667 | 305.3722 | 0.34644 | 1 | 90321.356 | 9385.0766 | 4027.3754 | 2689.0862 | NORMAL
324.8167 | 0.66667 | 305.3722 | 0.34644 | 1 | 106868.78 | 9506.6504 | 4332.9414 | 2689.0862 | NORMAL
324.8167 | 0.66667 | 305.3722 | 0.34644 | 2 | 57226.508 | 12364.4715 | 4124.6098 | 3622.6444 | NORMAL
324.8167 | 0.66667 | 305.3722 | 0.34644 | 2 | 73773.932 | 12555.3002 | 4605.9103 | 3622.6444 | NORMAL
324.8167 | 0.66667 | 305.3722 | 0.34644 | 2 | 90321.356 | 12732.4274 | 5092.7823 | 3622.6444 | NORMAL
324.8167 | 0.66667 | 305.3722 | 0.34644 | 2 | 106868.78 | 12897.3626 | 5574.1603 | 3622.6444 | NORMAL
324.8167 | 0.66667 | 305.3722 | 0.51403 | 1 | 57226.508 | 8740.4069 | 3901.1845 | 2770.2598 | NORMAL
324.8167 | 0.66667 | 305.3722 | 0.51403 | 1 | 73773.932 | 8875.3032 | 4133.094 | 2770.2598 | NORMAL
324.8167 | 0.66667 | 305.3722 | 0.51403 | 1 | 90321.356 | 9000.5138 | 4373.6167 | 2770.2598 | NORMAL
324.8167 | 0.66667 | 305.3722 | 0.51403 | 1 | 106868.78 | 9117.106 | 4613.7889 | 2770.2598 | NORMAL
324.8167 | 0.66667 | 305.3722 | 0.51403 | 2 | 57226.508 | 12603.078 | 4870.1995 | 4114.5477 | NORMAL
324.8167 | 0.66667 | 305.3722 | 0.51403 | 2 | 73773.932 | 12797.5893 | 5274.6039 | 4114.5477 | NORMAL
324.8167 | 0.66667 | 305.3722 | 0.51403 | 2 | 90321.356 | 12978.1346 | 5686.2365 | 4114.5477 | NORMAL
324.8167 | 0.66667 | 305.3722 | 0.51403 | 2 | 106868.78 | 13146.2528 | 6093.804 | 4114.5477 | NORMAL
324.8167 | 0.66667 | 305.3722 | 0.68163 | 1 | 57226.508 | 8350.8786 | 4227.4599 | 2737.9521 | NORMAL
324.8167 | 0.66667 | 305.3722 | 0.68163 | 1 | 73773.932 | 8479.763 | 4410.036 | 2737.9521 | NORMAL
324.8167 | 0.66667 | 305.3722 | 0.68163 | 1 | 90321.356 | 8599.3934 | 4605.0706 | 2737.9521 | NORMAL
324.8167 | 0.66667 | 305.3722 | 0.68163 | 1 | 106868.78 | 8710.7896 | 4802.562 | 2737.9521 | NORMAL
324.8167 | 0.66667 | 305.3722 | 0.68163 | 2 | 57226.508 | 12201.6294 | 5360.7412 | 4185.8253 | NORMAL
324.8167 | 0.66667 | 305.3722 | 0.68163 | 2 | 73773.932 | 12389.9449 | 5691.6716 | 4185.8253 | NORMAL
324.8167 | 0.66667 | 305.3722 | 0.68163 | 2 | 90321.356 | 12564.7392 | 6033.959 | 4185.8253 | NORMAL
324.8167 | 0.66667 | 305.3722 | 0.68163 | 2 | 106868.78 | 12727.5023 | 6375.3105 | 4185.8253 | NORMAL
324.8167 | 0.66667 | 305.3722 | 0.84923 | 1 | 57226.508 | 8049.7017 | 4463.4028 | 2691.8323 | NORMAL
324.8167 | 0.66667 | 305.3722 | 0.84923 | 1 | 73773.932 | 8173.9379 | 4611.6843 | 2691.8323 | NORMAL
324.8167 | 0.66667 | 305.3722 | 0.84923 | 1 | 90321.356 | 8289.2538 | 4775.5073 | 2691.8323 | NORMAL
324.8167 | 0.66667 | 305.3722 | 0.84923 | 1 | 106868.78 | 8396.6325 | 4944.0027 | 2691.8323 | NORMAL
324.8167 | 0.66667 | 305.3722 | 0.84923 | 2 | 57226.508 | 11787.4764 | 5728.6821 | 4160.3876 | NORMAL
324.8167 | 0.66667 | 305.3722 | 0.84923 | 2 | 73773.932 | 11969.4001 | 6004.2617 | 4160.3876 | NORMAL
324.8167 | 0.66667 | 305.3722 | 0.84923 | 2 | 90321.356 | 12138.2614 | 6295.338 | 4160.3876 | NORMAL
324.8167 | 0.66667 | 305.3722 | 0.84923 | 2 | 106868.78 | 12295.4999 | 6588.5112 | 4160.3876 | NORMAL
324.8167 | 1 | 291.4833 | 0.34644 | 1 | 57226.508 | 6420.4626 | 1493.0764 | 2616.6267 | NORMAL
324.8167 | 1 | 291.4833 | 0.34644 | 1 | 73773.932 | 6420.4626 | 1854.6777 | 2616.6267 | NORMAL
324.8167 | 1 | 291.4833 | 0.34644 | 1 | 90321.356 | 6420.4626 | 2179.8008 | 2616.6267 | NORMAL
324.8167 | 1 | 291.4833 | 0.34644 | 1 | 106868.78 | 6420.4626 | 2471.32 | 2616.6267 | NORMAL
324.8167 | 1 | 291.4833 | 0.34644 | 2 | 57226.508 | 8710.4322 | 2085.1285 | 3525.0295 | NORMAL
324.8167 | 1 | 291.4833 | 0.34644 | 2 | 73773.932 | 8710.4322 | 2603.513 | 3525.0295 | NORMAL
324.8167 | 1 | 291.4833 | 0.34644 | 2 | 90321.356 | 8710.4322 | 3070.8519 | 3525.0295 | NORMAL
324.8167 | 1 | 291.4833 | 0.34644 | 2 | 106868.78 | 8710.4322 | 3489.4754 | 3525.0295 | NORMAL
324.8167 | 1 | 291.4833 | 0.51403 | 1 | 57226.508 | 6157.3778 | 1393.9528 | 2695.6131 | NORMAL
324.8167 | 1 | 291.4833 | 0.51403 | 1 | 73773.932 | 6157.3778 | 1723.4057 | 2695.6131 | NORMAL
324.8167 | 1 | 291.4833 | 0.51403 | 1 | 90321.356 | 6157.3778 | 2018.7322 | 2695.6131 | NORMAL
324.8167 | 1 | 291.4833 | 0.51403 | 1 | 106868.78 | 6157.3778 | 2283.5315 | 2695.6131 | NORMAL
324.8167 | 1 | 291.4833 | 0.51403 | 2 | 57226.508 | 8878.524 | 2052.6677 | 4003.6782 | NORMAL
324.8167 | 1 | 291.4833 | 0.51403 | 2 | 73773.932 | 8878.524 | 2547.1635 | 4003.6782 | NORMAL
324.8167 | 1 | 291.4833 | 0.51403 | 2 | 90321.356 | 8878.524 | 2991.5001 | 4003.6782 | NORMAL
324.8167 | 1 | 291.4833 | 0.51403 | 2 | 106868.78 | 8878.524 | 3389.9376 | 4003.6782 | NORMAL
324.8167 | 1 | 291.4833 | 0.68163 | 1 | 57226.508 | 5882.9657 | 1314.6938 | 2664.1759 | NORMAL
324.8167 | 1 | 291.4833 | 0.68163 | 1 | 73773.932 | 5882.9657 | 1621.7731 | 2664.1759 | NORMAL
324.8167 | 1 | 291.4833 | 0.68163 | 1 | 90321.356 | 5882.9657 | 1896.6061 | 2664.1759 | NORMAL
324.8167 | 1 | 291.4833 | 0.68163 | 1 | 106868.78 | 5882.9657 | 2142.965 | 2664.1759 | NORMAL
324.8167 | 1 | 291.4833 | 0.68163 | 2 | 57226.508 | 8595.7145 | 1949.6989 | 4073.0352 | NORMAL
324.8167 | 1 | 291.4833 | 0.68163 | 2 | 73773.932 | 8595.7145 | 2411.3046 | 4073.0352 | NORMAL
324.8167 | 1 | 291.4833 | 0.68163 | 2 | 90321.356 | 8595.7145 | 2825.1897 | 4073.0352 | NORMAL
324.8167 | 1 | 291.4833 | 0.68163 | 2 | 106868.78 | 8595.7145 | 3196.302 | 4073.0352 | NORMAL
324.8167 | 1 | 291.4833 | 0.84923 | 1 | 57226.508 | 5670.7949 | 1257.9848 | 2619.2989 | NORMAL
324.8167 | 1 | 291.4833 | 0.84923 | 1 | 73773.932 | 5670.7949 | 1549.8563 | 2619.2989 | NORMAL
324.8167 | 1 | 291.4833 | 0.84923 | 1 | 90321.356 | 5670.7949 | 1810.834 | 2619.2989 | NORMAL
324.8167 | 1 | 291.4833 | 0.84923 | 1 | 106868.78 | 5670.7949 | 2044.7229 | 2619.2989 | NORMAL
324.8167 | 1 | 291.4833 | 0.84923 | 2 | 57226.508 | 8303.955 | 1862.7711 | 4048.2829 | NORMAL
324.8167 | 1 | 291.4833 | 0.84923 | 2 | 73773.932 | 8303.955 | 2299.3713 | 4048.2829 | NORMAL
324.8167 | 1 | 291.4833 | 0.84923 | 2 | 90321.356 | 8303.955 | 2690.3093 | 4048.2829 | NORMAL
324.8167 | 1 | 291.4833 | 0.84923 | 2 | 106868.78 | 8303.955 | 3040.7767 | 4048.2829 | NORMAL
324.8167 | 1 | 296.113 | 0.34644 | 1 | 57226.508 | 7596.4488 | 1419.7819 | 2689.0862 | NORMAL
324.8167 | 1 | 296.113 | 0.34644 | 1 | 73773.932 | 7596.4488 | 1792.6885 | 2689.0862 | NORMAL
324.8167 | 1 | 296.113 | 0.34644 | 1 | 90321.356 | 7596.4488 | 2138.3746 | 2689.0862 | NORMAL
324.8167 | 1 | 296.113 | 0.34644 | 1 | 106868.78 | 7596.4488 | 2457.3657 | 2689.0862 | NORMAL
324.8167 | 1 | 296.113 | 0.34644 | 2 | 57226.508 | 10305.8544 | 1980.2517 | 3622.6444 | NORMAL
324.8167 | 1 | 296.113 | 0.34644 | 2 | 73773.932 | 10305.8544 | 2516.1038 | 3622.6444 | NORMAL
324.8167 | 1 | 296.113 | 0.34644 | 2 | 90321.356 | 10305.8544 | 3016.1289 | 3622.6444 | NORMAL
324.8167 | 1 | 296.113 | 0.34644 | 2 | 106868.78 | 10305.8544 | 3478.9073 | 3622.6444 | NORMAL
324.8167 | 1 | 296.113 | 0.51403 | 1 | 57226.508 | 7285.1768 | 1327.1707 | 2770.2598 | NORMAL
324.8167 | 1 | 296.113 | 0.51403 | 1 | 73773.932 | 7285.1768 | 1666.3523 | 2770.2598 | NORMAL
324.8167 | 1 | 296.113 | 0.51403 | 1 | 90321.356 | 7285.1768 | 1978.8316 | 2770.2598 | NORMAL
324.8167 | 1 | 296.113 | 0.51403 | 1 | 106868.78 | 7285.1768 | 2266.2398 | 2770.2598 | NORMAL
324.8167 | 1 | 296.113 | 0.51403 | 2 | 57226.508 | 10504.7342 | 1952.421 | 4114.5477 | NORMAL
324.8167 | 1 | 296.113 | 0.51403 | 2 | 73773.932 | 10504.7342 | 2462.1704 | 4114.5477 | NORMAL
324.8167 | 1 | 296.113 | 0.51403 | 2 | 90321.356 | 10504.7342 | 2934.0748 | 4114.5477 | NORMAL
324.8167 | 1 | 296.113 | 0.51403 | 2 | 106868.78 | 10504.7342 | 3369.2431 | 4114.5477 | NORMAL
324.8167 | 1 | 296.113 | 0.68163 | 1 | 57226.508 | 6960.5028 | 1252.4822 | 2737.9521 | NORMAL
324.8167 | 1 | 296.113 | 0.68163 | 1 | 73773.932 | 6960.5028 | 1568.4215 | 2737.9521 | NORMAL
324.8167 | 1 | 296.113 | 0.68163 | 1 | 90321.356 | 6960.5028 | 1858.6203 | 2737.9521 | NORMAL
324.8167 | 1 | 296.113 | 0.68163 | 1 | 106868.78 | 6960.5028 | 2125.0828 | 2737.9521 | NORMAL
324.8167 | 1 | 296.113 | 0.68163 | 2 | 57226.508 | 10170.1246 | 1856.1239 | 4185.8253 | NORMAL
324.8167 | 1 | 296.113 | 0.68163 | 2 | 73773.932 | 10170.1246 | 2331.411 | 4185.8253 | NORMAL
324.8167 | 1 | 296.113 | 0.68163 | 2 | 90321.356 | 10170.1246 | 2769.4751 | 4185.8253 | NORMAL
324.8167 | 1 | 296.113 | 0.68163 | 2 | 106868.78 | 10170.1246 | 3172.4909 | 4185.8253 | NORMAL
324.8167 | 1 | 296.113 | 0.84923 | 1 | 57226.508 | 6709.4703 | 1198.8837 | 2691.8323 | NORMAL
324.8167 | 1 | 296.113 | 0.84923 | 1 | 73773.932 | 6709.4703 | 1499.0764 | 2691.8323 | NORMAL
324.8167 | 1 | 296.113 | 0.84923 | 1 | 90321.356 | 6709.4703 | 1774.3455 | 2691.8323 | NORMAL
324.8167 | 1 | 296.113 | 0.84923 | 1 | 106868.78 | 6709.4703 | 2026.849 | 2691.8323 | NORMAL
324.8167 | 1 | 296.113 | 0.84923 | 2 | 57226.508 | 9824.9258 | 1774.3014 | 4160.3876 | NORMAL
324.8167 | 1 | 296.113 | 0.84923 | 2 | 73773.932 | 9824.9258 | 2223.5808 | 4160.3876 | NORMAL
324.8167 | 1 | 296.113 | 0.84923 | 2 | 90321.356 | 9824.9258 | 2636.6166 | 4160.3876 | NORMAL
324.8167 | 1 | 296.113 | 0.84923 | 2 | 106868.78 | 9824.9258 | 3016.0597 | 4160.3876 | NORMAL
324.8167 | 1 | 300.7426 | 0.34644 | 1 | 57226.508 | 9844.7173 | 1483.0449 | 2689.0862 | NORMAL
324.8167 | 1 | 300.7426 | 0.34644 | 1 | 73773.932 | 9844.7173 | 1904.173 | 2689.0862 | NORMAL
324.8167 | 1 | 300.7426 | 0.34644 | 1 | 90321.356 | 9844.7173 | 2305.8527 | 2689.0862 | NORMAL
324.8167 | 1 | 300.7426 | 0.34644 | 1 | 106868.78 | 9844.7173 | 2686.704 | 2689.0862 | NORMAL
324.8167 | 1 | 300.7426 | 0.34644 | 2 | 57226.508 | 13356.0069 | 2070.9542 | 3622.6444 | NORMAL
324.8167 | 1 | 300.7426 | 0.34644 | 2 | 73773.932 | 13356.0069 | 2680.3284 | 3622.6444 | NORMAL
324.8167 | 1 | 300.7426 | 0.34644 | 2 | 90321.356 | 13356.0069 | 3268.06 | 3622.6444 | NORMAL
324.8167 | 1 | 300.7426 | 0.34644 | 2 | 106868.78 | 13356.0069 | 3829.4665 | 3622.6444 | NORMAL
324.8167 | 1 | 300.7426 | 0.51403 | 1 | 57226.508 | 9441.3202 | 1385.0205 | 2770.2598 | NORMAL
324.8167 | 1 | 300.7426 | 0.51403 | 1 | 73773.932 | 9441.3202 | 1765.8811 | 2770.2598 | NORMAL
324.8167 | 1 | 300.7426 | 0.51403 | 1 | 90321.356 | 9441.3202 | 2125.5857 | 2770.2598 | NORMAL
324.8167 | 1 | 300.7426 | 0.51403 | 1 | 106868.78 | 9441.3202 | 2464.2797 | 2770.2598 | NORMAL
324.8167 | 1 | 300.7426 | 0.51403 | 2 | 57226.508 | 13613.7478 | 2038.9768 | 4114.5477 | NORMAL
324.8167 | 1 | 300.7426 | 0.51403 | 2 | 73773.932 | 13613.7478 | 2613.8945 | 4114.5477 | NORMAL
324.8167 | 1 | 300.7426 | 0.51403 | 2 | 90321.356 | 13613.7478 | 3161.064 | 4114.5477 | NORMAL
324.8167 | 1 | 300.7426 | 0.51403 | 2 | 106868.78 | 13613.7478 | 3679.0764 | 4114.5477 | NORMAL
324.8167 | 1 | 300.7426 | 0.68163 | 1 | 57226.508 | 9020.5547 | 1306.5664 | 2737.9521 | NORMAL
324.8167 | 1 | 300.7426 | 0.68163 | 1 | 73773.932 | 9020.5547 | 1660.4373 | 2737.9521 | NORMAL
324.8167 | 1 | 300.7426 | 0.68163 | 1 | 90321.356 | 9020.5547 | 1993.1219 | 2737.9521 | NORMAL
324.8167 | 1 | 300.7426 | 0.68163 | 1 | 106868.78 | 9020.5547 | 2305.34 | 2737.9521 | NORMAL
324.8167 | 1 | 300.7426 | 0.68163 | 2 | 57226.508 | 13180.1061 | 1937.1482 | 4185.8253 | NORMAL
324.8167 | 1 | 300.7426 | 0.68163 | 2 | 73773.932 | 13180.1061 | 2471.0449 | 4185.8253 | NORMAL
324.8167 | 1 | 300.7426 | 0.68163 | 2 | 90321.356 | 13180.1061 | 2975.6326 | 4185.8253 | NORMAL
324.8167 | 1 | 300.7426 | 0.68163 | 2 | 106868.78 | 13180.1061 | 3450.9812 | 4185.8253 | NORMAL
324.8167 | 1 | 300.7426 | 0.84923 | 1 | 57226.508 | 8695.2258 | 1250.396 | 2691.8323 | NORMAL
324.8167 | 1 | 300.7426 | 0.84923 | 1 | 73773.932 | 8695.2258 | 1586.1714 | 2691.8323 | NORMAL
324.8167 | 1 | 300.7426 | 0.84923 | 1 | 90321.356 | 8695.2258 | 1901.0381 | 2691.8323 | NORMAL
324.8167 | 1 | 300.7426 | 0.84923 | 1 | 106868.78 | 8695.2258 | 2195.9855 | 2691.8323 | NORMAL
324.8167 | 1 | 300.7426 | 0.84923 | 2 | 57226.508 | 12732.7413 | 1851.123 | 4160.3876 | NORMAL
324.8167 | 1 | 300.7426 | 0.84923 | 2 | 73773.932 | 12732.7413 | 2354.7058 | 4160.3876 | NORMAL
324.8167 | 1 | 300.7426 | 0.84923 | 2 | 90321.356 | 12732.7413 | 2828.7693 | 4160.3876 | NORMAL
324.8167 | 1 | 300.7426 | 0.84923 | 2 | 106868.78 | 12732.7413 | 3274.0978 | 4160.3876 | NORMAL
324.8167 | 1 | 305.3722 | 0.34644 | 1 | 57226.508 | 13165.268 | 1595.4886 | 2689.0862 | NORMAL
324.8167 | 1 | 305.3722 | 0.34644 | 1 | 73773.932 | 13165.268 | 2083.6548 | 2689.0862 | NORMAL
324.8167 | 1 | 305.3722 | 0.34644 | 1 | 90321.356 | 13165.268 | 2562.1376 | 2689.0862 | NORMAL
324.8167 | 1 | 305.3722 | 0.34644 | 1 | 106868.78 | 13165.268 | 3028.1149 | 2689.0862 | NORMAL
324.8167 | 1 | 305.3722 | 0.34644 | 2 | 57226.508 | 17860.8897 | 2232.1089 | 3622.6444 | NORMAL
324.8167 | 1 | 305.3722 | 0.34644 | 2 | 73773.932 | 17860.8897 | 2944.7467 | 3622.6444 | NORMAL
324.8167 | 1 | 305.3722 | 0.34644 | 2 | 90321.356 | 17860.8897 | 3655.0882 | 3622.6444 | NORMAL
324.8167 | 1 | 305.3722 | 0.34644 | 2 | 106868.78 | 17860.8897 | 4356.1814 | 3622.6444 | NORMAL
324.8167 | 1 | 305.3722 | 0.51403 | 1 | 57226.508 | 12625.8081 | 1487.8461 | 2770.2598 | NORMAL
324.8167 | 1 | 305.3722 | 0.51403 | 1 | 73773.932 | 12625.8081 | 1926.2016 | 2770.2598 | NORMAL
324.8167 | 1 | 305.3722 | 0.51403 | 1 | 90321.356 | 12625.8081 | 2349.7607 | 2770.2598 | NORMAL
324.8167 | 1 | 305.3722 | 0.51403 | 1 | 106868.78 | 12625.8081 | 2757.4972 | 2770.2598 | NORMAL
324.8167 | 1 | 305.3722 | 0.51403 | 2 | 57226.508 | 18205.5648 | 2192.8266 | 4114.5477 | NORMAL
324.8167 | 1 | 305.3722 | 0.51403 | 2 | 73773.932 | 18205.5648 | 2858.1768 | 4114.5477 | NORMAL
324.8167 | 1 | 305.3722 | 0.51403 | 2 | 90321.356 | 18205.5648 | 3508.2352 | 4114.5477 | NORMAL
324.8167 | 1 | 305.3722 | 0.51403 | 2 | 106868.78 | 18205.5648 | 4139.6635 | 4114.5477 | NORMAL
324.8167 | 1 | 305.3722 | 0.68163 | 1 | 57226.508 | 12063.1215 | 1402.6881 | 2737.9521 | NORMAL
324.8167 | 1 | 305.3722 | 0.68163 | 1 | 73773.932 | 12063.1215 | 1808.7175 | 2737.9521 | NORMAL
324.8167 | 1 | 305.3722 | 0.68163 | 1 | 90321.356 | 12063.1215 | 2198.5116 | 2737.9521 | NORMAL
324.8167 | 1 | 305.3722 | 0.68163 | 1 | 106868.78 | 12063.1215 | 2571.7728 | 2737.9521 | NORMAL
324.8167 | 1 | 305.3722 | 0.68163 | 2 | 57226.508 | 17625.659 | 2081.1669 | 4185.8253 | NORMAL
324.8167 | 1 | 305.3722 | 0.68163 | 2 | 73773.932 | 17625.659 | 2695.9545 | 4185.8253 | NORMAL
324.8167 | 1 | 305.3722 | 0.68163 | 2 | 90321.356 | 17625.659 | 3290.5737 | 4185.8253 | NORMAL
324.8167 | 1 | 305.3722 | 0.68163 | 2 | 106868.78 | 17625.659 | 3863.4376 | 4185.8253 | NORMAL
324.8167 | 1 | 305.3722 | 0.84923 | 1 | 57226.508 | 11628.0615 | 1341.9374 | 2691.8323 | NORMAL
324.8167 | 1 | 305.3722 | 0.84923 | 1 | 73773.932 | 11628.0615 | 1726.5596 | 2691.8323 | NORMAL
324.8167 | 1 | 305.3722 | 0.84923 | 1 | 90321.356 | 11628.0615 | 2094.4911 | 2691.8323 | NORMAL
324.8167 | 1 | 305.3722 | 0.84923 | 1 | 106868.78 | 11628.0615 | 2445.7968 | 2691.8323 | NORMAL
324.8167 | 1 | 305.3722 | 0.84923 | 2 | 57226.508 | 17027.4012 | 1987.6609 | 4160.3876 | NORMAL
324.8167 | 1 | 305.3722 | 0.84923 | 2 | 73773.932 | 17027.4012 | 2565.9816 | 4160.3876 | NORMAL
324.8167 | 1 | 305.3722 | 0.84923 | 2 | 90321.356 | 17027.4012 | 3122.2148 | 4160.3876 | NORMAL
324.8167 | 1 | 305.3722 | 0.84923 | 2 | 106868.78 | 17027.4012 | 3655.6657 | 4160.3876 | NORMAL
Note on A2: Data group defining the grid variables for cooling performance
Note on G2: Data group defining the lookup variables for cooling performance
Note on A3: Dry bulb temperature of the air entering the outdoor coil
Note on B3: Relative humidity of the air entering the indoor coil
Note on C3: Dry bulb temperature of the air entering the indoor coil
Note on D3: Mass flow rate of air entering the indoor coil
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Ambient absolute air pressure
Note on G3: Total heat removed by the indoor coil
Note on H3: Sensible heat removed by the indoor coil
Note on I3: Gross power draw (of the outdoor unit)
Note on J3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
outdoor_coil_environment_dry_bulb_temperature | gross_power
K | W
282.65 | 30
283.65 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the outdoor coil
Note on B3: Gross power draw (of the outdoor unit)