## RS0001
RS0001: Liquid-Cooled Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 2.0.0 |  | ✓
| description | ASHRAE 90.1-2019 Addendum 'bd' curve set 'AB': 300.0+ ton, 6.10 COP, 6.40 IPLV liquid-cooled, centrifugal compressor chiller |  | ✓
| id | 7b69b8c6-f30f-4099-a6e4-d17663e83e1c |  | ✓
| data_timestamp | 2024-02-22T13:52Z |  | ✓
| data_version | 2 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2019 Addendum 'bd' curve set 'AB' for Performance Rating Method (PRM)
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | CENTRIFUGAL
performance |  |  |  | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
performance.condenser_liquid_type |  |  |  | ✓
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
| condenser_fouling_factor | 0 | m2-K/W | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| cycling_degradation_coefficient | 0 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
performance.performance_map_evaporator_liquid_pressure_differential |  | $performance_map_evaporator_liqu |  | ✓
performance.performance_map_condenser_liquid_pressure_differential |  | $performance_map_condenser_liqui |  | ✓
performance.scaling
| minimum | 0.85714 | -
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on A20: Type of liquid in evaporator
Note on A21: An array of all liquid components within the liquid mixture
Note on B22: Defines whether concentration is defined on a volume or mass basis
Note on A23: Type of liquid in condenser
Note on A24: An array of all liquid components within the liquid mixture
Note on B25: Defines whether concentration is defined on a volume or mass basis
Note on B26: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B27: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B28: Type of compressor speed control
Note on B29: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A30: Data group describing cooling performance over a range of conditions
Note on A31: Data group describing standby performance
Note on A32: Data group describing the liquid pressure differential through the evaporator
Note on A33: Data group describing the liquid pressure differential through the condenser
Note on A34: Specifies the range the performance data can be scaled to represent different capacity equipment
Note on B35: Minimum scaling factor

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | oil_cooler_heat | auxiliary_heat | operation_state
m3/s | K | m3/s | K | - | W | W | W | W | W | -
0.052741 | 277.0389 | 0.066619 | 285.9278 | 1 | 64962.4359 | 321295.9475 | 386258.3834 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.066619 | 285.9278 | 2 | 88619.413 | 642591.895 | 731211.308 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.066619 | 285.9278 | 3 | 123689.3145 | 963887.8425 | 1087577.157 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.066619 | 285.9278 | 4 | 170172.1404 | 1285183.7901 | 1455355.9304 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.066619 | 295.0019 | 1 | 74306.8492 | 303192.1191 | 377498.9683 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.066619 | 295.0019 | 2 | 101366.7247 | 606384.2383 | 707750.9629 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.066619 | 295.0019 | 3 | 141481.1977 | 909576.3574 | 1051057.5551 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.066619 | 295.0019 | 4 | 194650.2682 | 1212768.4765 | 1407418.7447 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.066619 | 304.0759 | 1 | 75008.8332 | 277639.0111 | 352647.8443 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.066619 | 304.0759 | 2 | 102324.346 | 555278.0221 | 657602.3681 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.066619 | 304.0759 | 3 | 142817.7843 | 832917.0332 | 975734.8175 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.066619 | 304.0759 | 4 | 196489.1481 | 1110556.0443 | 1307045.1924 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.066619 | 313.15 | 1 | 67872.9345 | 244636.6233 | 312509.5578 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.066619 | 313.15 | 2 | 92589.8102 | 489273.2466 | 581863.0568 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.066619 | 313.15 | 3 | 129230.9412 | 733909.8699 | 863140.8111 | 0 | 0 | NORMAL
0.052741 | 277.0389 | 0.066619 | 313.15 | 4 | 177796.3275 | 978546.4932 | 1156342.8207 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.066619 | 285.9278 | 1 | 62022.5703 | 344598.094 | 406620.6642 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.066619 | 285.9278 | 2 | 84608.9543 | 689196.1879 | 773805.1422 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.066619 | 285.9278 | 3 | 118091.7724 | 1033794.2819 | 1151886.0543 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.066619 | 285.9278 | 4 | 162471.0248 | 1378392.3759 | 1540863.4007 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.066619 | 295.0019 | 1 | 73912.5225 | 331956.3468 | 405868.8693 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.066619 | 295.0019 | 2 | 100828.7985 | 663912.6935 | 764741.492 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.066619 | 295.0019 | 3 | 140730.3946 | 995869.0403 | 1136599.4349 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.066619 | 295.0019 | 4 | 193617.311 | 1327825.3871 | 1521442.6981 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.066619 | 304.0759 | 1 | 77193.3897 | 311865.3199 | 389058.7096 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.066619 | 304.0759 | 2 | 105304.4392 | 623730.6397 | 729035.079 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.066619 | 304.0759 | 3 | 146977.208 | 935595.9596 | 1082573.1676 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.066619 | 304.0759 | 4 | 202211.6962 | 1247461.2795 | 1449672.9757 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.066619 | 313.15 | 1 | 72382.8487 | 284325.0133 | 356707.8619 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.066619 | 313.15 | 2 | 98742.0725 | 568650.0266 | 667392.0991 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.066619 | 313.15 | 3 | 137817.8759 | 852975.0398 | 990792.9157 | 0 | 0 | NORMAL
0.052741 | 280.9278 | 0.066619 | 313.15 | 4 | 189610.2588 | 1137300.0531 | 1326910.3119 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.066619 | 285.9278 | 1 | 58488.042 | 353473.2723 | 411961.3142 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.066619 | 285.9278 | 2 | 79787.2782 | 706946.5445 | 786733.8227 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.066619 | 285.9278 | 3 | 111361.9851 | 1060419.8168 | 1171781.8018 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.066619 | 285.9278 | 4 | 153212.1626 | 1413893.089 | 1567105.2516 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.066619 | 295.0019 | 1 | 72000.6552 | 346293.6062 | 418294.2614 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.066619 | 295.0019 | 2 | 98220.6979 | 692587.2125 | 790807.9104 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.066619 | 295.0019 | 3 | 137090.1746 | 1038880.8187 | 1175970.9933 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.066619 | 295.0019 | 4 | 188609.085 | 1385174.4249 | 1573783.51 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.066619 | 304.0759 | 1 | 77132.3695 | 331664.6605 | 408797.03 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.066619 | 304.0759 | 2 | 105221.1976 | 663329.321 | 768550.5186 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.066619 | 304.0759 | 3 | 146861.0247 | 994993.9815 | 1141855.0063 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.066619 | 304.0759 | 4 | 202051.8508 | 1326658.642 | 1528710.4929 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.066619 | 313.15 | 1 | 74113.992 | 309586.4351 | 383700.4271 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.066619 | 313.15 | 2 | 101103.6359 | 619172.8702 | 720276.5061 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.066619 | 313.15 | 3 | 141113.9951 | 928759.3053 | 1069873.3004 | 0 | 0 | NORMAL
0.052741 | 284.8167 | 0.066619 | 313.15 | 4 | 194145.0698 | 1238345.7404 | 1432490.8101 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.066619 | 285.9278 | 1 | 55191.8445 | 347921.4824 | 403113.3269 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.066619 | 285.9278 | 2 | 75290.7245 | 695842.9648 | 771133.6892 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.066619 | 285.9278 | 3 | 105085.9827 | 1043764.4471 | 1148850.4298 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.066619 | 285.9278 | 4 | 144577.6191 | 1391685.9295 | 1536263.5486 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.066619 | 295.0019 | 1 | 69539.7261 | 346203.8975 | 415743.6236 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.066619 | 295.0019 | 2 | 94863.5872 | 692407.7951 | 787271.3823 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.066619 | 295.0019 | 3 | 132404.5339 | 1038611.6926 | 1171016.2265 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.066619 | 295.0019 | 4 | 182162.5662 | 1384815.5901 | 1566978.1563 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.066619 | 304.0759 | 1 | 75929.737 | 337037.033 | 412966.77 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.066619 | 304.0759 | 2 | 103580.6097 | 674074.066 | 777654.6757 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.066619 | 304.0759 | 3 | 144571.1969 | 1011111.0989 | 1155682.2959 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.066619 | 304.0759 | 4 | 198901.4987 | 1348148.1319 | 1547049.6306 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.066619 | 313.15 | 1 | 74305.8145 | 320420.8887 | 394726.7032 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.066619 | 313.15 | 2 | 101365.3132 | 640841.7775 | 742207.0907 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.066619 | 313.15 | 3 | 141479.2276 | 961262.6662 | 1102741.8938 | 0 | 0 | NORMAL
0.052741 | 288.7056 | 0.066619 | 313.15 | 4 | 194647.5578 | 1281683.5549 | 1476331.1127 | 0 | 0 | NORMAL
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on J3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).
Note on K3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation

## performance_map_evaporator_liqu
performance.performance_map_evaporator_liquid_pressure_differential
grid_variables |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | evaporator_liquid_differential_pressure
m3/s | K | Pa
0.052741 | 277.0389 | 15000
0.052741 | 280.9278 | 15000
0.052741 | 284.8167 | 15000
0.052741 | 288.7056 | 15000
Note on A2: Data group defining the grid variables for the evaporator liquid pressure differential
Note on C2: Data group defining the lookup variables for the evaporator liquid pressure differential
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Pressure difference across the evaporator

## performance_map_condenser_liqui
performance.performance_map_condenser_liquid_pressure_differential
grid_variables |  | lookup_variables
condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | condenser_liquid_differential_pressure
m3/s | K | Pa
0.066619 | 285.9278 | 15000
0.066619 | 295.0019 | 15000
0.066619 | 304.0759 | 15000
0.066619 | 313.15 | 15000
Note on A2: Data group defining the grid variables for the condenser liquid pressure differential
Note on C2: Data group defining the lookup variables for the condenser liquid pressure differential
Note on A3: Condenser liquid flow
Note on B3: Entering condenser liquid temperature
Note on C3: Pressure difference across the condenser