## RS0001
RS0001: Liquid-Cooled Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 2.0.0 |  | ✓
| description | ASHRAE 90.1-2019 Addendum 'bd' curve set 'P': 300.0-600.0 ton, 5.63 COP, 8.58 IPLV liquid-cooled, positive displacement compressor chiller |  | ✓
| id | 22bf295a-f0a6-4223-bceb-57b4f20edff9 |  | ✓
| data_timestamp | 2024-02-22T13:52Z |  | ✓
| data_version | 2 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2019 Addendum 'bd' curve set 'P' for Energy Cost Budget (ECB) Path B
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | SCROLL
performance |  |  |  | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
performance.condenser_liquid_type |  |  |  | ✓
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
| condenser_fouling_factor | 0 | m2-K/W | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| cycling_degradation_coefficient | 0 | - | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
performance.performance_map_evaporator_liquid_pressure_differential |  | $performance_map_evaporator_liqu |  | ✓
performance.performance_map_condenser_liquid_pressure_differential |  | $performance_map_condenser_liqui |  | ✓
performance.scaling
| minimum | 0.66667 | -
| maximum | 1.3333 | -
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on A20: Type of liquid in evaporator
Note on A21: An array of all liquid components within the liquid mixture
Note on B22: Defines whether concentration is defined on a volume or mass basis
Note on A23: Type of liquid in condenser
Note on A24: An array of all liquid components within the liquid mixture
Note on B25: Defines whether concentration is defined on a volume or mass basis
Note on B26: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B27: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B28: Type of compressor speed control
Note on B29: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A30: Data group describing cooling performance over a range of conditions
Note on A31: Data group describing standby performance
Note on A32: Data group describing the liquid pressure differential through the evaporator
Note on A33: Data group describing the liquid pressure differential through the condenser
Note on A34: Specifies the range the performance data can be scaled to represent different capacity equipment
Note on B35: Minimum scaling factor
Note on B36: Maximum scaling factor

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | oil_cooler_heat | auxiliary_heat | operation_state
m3/s | K | m3/s | K | - | W | W | W | W | W | -
0.067809 | 277.0389 | 0.086666 | 285.9278 | 1 | 40408.7581 | 392817.2434 | 433226.0015 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.086666 | 285.9278 | 2 | 78539.6377 | 785634.4869 | 864174.1245 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.086666 | 285.9278 | 3 | 136766.4763 | 1178451.7303 | 1315218.2066 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.086666 | 285.9278 | 4 | 215089.274 | 1571268.9738 | 1786358.2477 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.086666 | 295.0019 | 1 | 47728.2867 | 385973.2759 | 433701.5626 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.086666 | 295.0019 | 2 | 92766.0864 | 771946.5518 | 864712.6382 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.086666 | 295.0019 | 3 | 161539.9705 | 1157919.8277 | 1319459.7982 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.086666 | 295.0019 | 4 | 254049.9391 | 1543893.1036 | 1797943.0427 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.086666 | 304.0759 | 1 | 53577.147 | 367792.5037 | 421369.6507 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.086666 | 304.0759 | 2 | 104134.1013 | 735585.0074 | 839719.1087 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.086666 | 304.0759 | 3 | 181335.8773 | 1103377.5111 | 1284713.3883 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.086666 | 304.0759 | 4 | 285182.4749 | 1471170.0148 | 1756352.4896 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.086666 | 313.15 | 1 | 57139.6479 | 338274.9268 | 395414.5747 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.086666 | 313.15 | 2 | 111058.2817 | 676549.8536 | 787608.1354 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.086666 | 313.15 | 3 | 193393.4292 | 1014824.7805 | 1208218.2097 | 0 | 0 | NORMAL
0.067809 | 277.0389 | 0.086666 | 313.15 | 4 | 304145.0903 | 1353099.7073 | 1657244.7976 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.086666 | 285.9278 | 1 | 39440.0732 | 418500.628 | 457940.7012 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.086666 | 285.9278 | 2 | 76656.8736 | 837001.2559 | 913658.1295 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.086666 | 285.9278 | 3 | 133487.8896 | 1255501.8839 | 1388989.7735 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.086666 | 285.9278 | 4 | 209933.1213 | 1674002.5118 | 1883935.6331 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.086666 | 295.0019 | 1 | 47047.0341 | 414895.7475 | 461942.7815 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.086666 | 295.0019 | 2 | 91441.9839 | 829791.4949 | 921233.4788 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.086666 | 295.0019 | 3 | 159234.2198 | 1244687.2424 | 1403921.4621 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.086666 | 295.0019 | 4 | 250423.7417 | 1659582.9898 | 1910006.7315 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.086666 | 304.0759 | 1 | 53504.1206 | 399954.0623 | 453458.1829 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.086666 | 304.0759 | 2 | 103992.1651 | 799908.1246 | 903900.2897 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.086666 | 304.0759 | 3 | 181088.7141 | 1199862.1869 | 1380950.901 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.086666 | 304.0759 | 4 | 284793.7674 | 1599816.2492 | 1884610.0166 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.086666 | 313.15 | 1 | 58063.1554 | 373675.5725 | 431738.7279 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.086666 | 313.15 | 2 | 112853.2378 | 747351.1449 | 860204.3827 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.086666 | 313.15 | 3 | 196519.1097 | 1121026.7174 | 1317545.8271 | 0 | 0 | NORMAL
0.067809 | 280.9278 | 0.086666 | 313.15 | 4 | 309060.7711 | 1494702.2899 | 1803763.061 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.086666 | 285.9278 | 1 | 39060.4771 | 429141.405 | 468201.8821 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.086666 | 285.9278 | 2 | 75919.0795 | 858282.81 | 934201.8895 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.086666 | 285.9278 | 3 | 132203.118 | 1287424.215 | 1419627.333 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.086666 | 285.9278 | 4 | 207912.5926 | 1716565.6201 | 1924478.2127 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.086666 | 295.0019 | 1 | 46538.9262 | 428775.6116 | 475314.5377 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.086666 | 295.0019 | 2 | 90454.4106 | 857551.2231 | 948005.6337 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.086666 | 295.0019 | 3 | 157514.4904 | 1286326.8347 | 1443841.3251 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.086666 | 295.0019 | 4 | 247719.1656 | 1715102.4463 | 1962821.6118 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.086666 | 304.0759 | 1 | 53087.3646 | 417073.0134 | 470160.3781 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.086666 | 304.0759 | 2 | 103182.1461 | 834146.0269 | 937328.173 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.086666 | 304.0759 | 3 | 179678.1722 | 1251219.0403 | 1430897.2126 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.086666 | 304.0759 | 4 | 282575.4429 | 1668292.0538 | 1950867.4967 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.086666 | 313.15 | 1 | 58025.1286 | 394033.6107 | 452058.7393 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.086666 | 313.15 | 2 | 112779.3278 | 788067.2213 | 900846.5491 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.086666 | 313.15 | 3 | 196390.4051 | 1182100.832 | 1378491.2371 | 0 | 0 | NORMAL
0.067809 | 284.8167 | 0.086666 | 313.15 | 4 | 308858.3606 | 1576134.4427 | 1884992.8033 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.086666 | 285.9278 | 1 | 39587.926 | 424739.5746 | 464327.5007 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.086666 | 285.9278 | 2 | 76944.2446 | 849479.1492 | 926423.3938 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.086666 | 285.9278 | 3 | 133988.3085 | 1274218.7238 | 1408207.0324 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.086666 | 285.9278 | 4 | 210720.1179 | 1698958.2985 | 1909678.4163 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.086666 | 295.0019 | 1 | 46648.2121 | 427612.8682 | 474261.0804 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.086666 | 295.0019 | 2 | 90666.822 | 855225.7364 | 945892.5585 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.086666 | 295.0019 | 3 | 157884.3771 | 1282838.6046 | 1440722.9817 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.086666 | 295.0019 | 4 | 248300.8772 | 1710451.4728 | 1958752.35 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.086666 | 304.0759 | 1 | 52897.421 | 419149.3571 | 472046.7782 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.086666 | 304.0759 | 2 | 102812.9662 | 838298.7143 | 941111.6805 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.086666 | 304.0759 | 3 | 179035.2938 | 1257448.0714 | 1436483.3653 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.086666 | 304.0759 | 4 | 281564.4039 | 1676597.4286 | 1958161.8325 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.086666 | 313.15 | 1 | 57722.4023 | 399349.0414 | 457071.4437 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.086666 | 313.15 | 2 | 112190.9401 | 798698.0828 | 910889.0229 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.086666 | 313.15 | 3 | 195365.8052 | 1198047.1242 | 1393412.9294 | 0 | 0 | NORMAL
0.067809 | 288.7056 | 0.086666 | 313.15 | 4 | 307246.9975 | 1597396.1656 | 1904643.1632 | 0 | 0 | NORMAL
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on J3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).
Note on K3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation

## performance_map_evaporator_liqu
performance.performance_map_evaporator_liquid_pressure_differential
grid_variables |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | evaporator_liquid_differential_pressure
m3/s | K | Pa
0.067809 | 277.0389 | 15000
0.067809 | 280.9278 | 15000
0.067809 | 284.8167 | 15000
0.067809 | 288.7056 | 15000
Note on A2: Data group defining the grid variables for the evaporator liquid pressure differential
Note on C2: Data group defining the lookup variables for the evaporator liquid pressure differential
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Pressure difference across the evaporator

## performance_map_condenser_liqui
performance.performance_map_condenser_liquid_pressure_differential
grid_variables |  | lookup_variables
condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | condenser_liquid_differential_pressure
m3/s | K | Pa
0.086666 | 285.9278 | 15000
0.086666 | 295.0019 | 15000
0.086666 | 304.0759 | 15000
0.086666 | 313.15 | 15000
Note on A2: Data group defining the grid variables for the condenser liquid pressure differential
Note on C2: Data group defining the lookup variables for the condenser liquid pressure differential
Note on A3: Condenser liquid flow
Note on B3: Entering condenser liquid temperature
Note on C3: Pressure difference across the condenser