## RS0001
RS0001: Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 3.0.0 |  | ✓
| description | ASHRAE 90.1-2022 Appendix J curve set 'A': 0.0-150.0 ton, 2.96 COP, 4.02 IPLV air-cooled, compressor chiller |  | ✓
| id | f2801741-4d23-48e5-ad8e-29e92295b585 |  | ✓
| data_timestamp | 2025-02-18T13:40Z |  | ✓
| data_version | 3 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2022 Appendix J curve set 'A' for Energy Cost Budget (ECB) Path A
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
performance |  |  |  | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| cycling_degradation_coefficient | 0 | - | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
performance.performance_map_evaporator_liquid_pressure_differential |  | $performance_map_evaporator_liqu |  | ✓
| condenser_type | AIR |  | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
performance.scaling
| maximum | 2 | -
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on A18: Data group containing performance information
Note on B19: Type of compressor speed control
Note on B20: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A21: Type of liquid in evaporator
Note on A22: An array of all liquid components within the liquid mixture
Note on B23: Defines whether concentration is defined on a volume or mass basis
Note on B24: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on A25: Data group describing the liquid pressure differential through the evaporator
Note on B26: Heat rejection method of the condenser
Note on A27: Data group describing cooling performance over a range of conditions
Note on A28: Data group describing standby performance
Note on A29: Specifies the range the performance data can be scaled to represent different capacity equipment
Note on B30: Maximum scaling factor

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_evaporator_liqu
performance.performance_map_evaporator_liquid_pressure_differential
grid_variables |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | evaporator_liquid_differential_pressure
m3/s | K | Pa
0.011302 | 275.3722 | 15000
0.011302 | 281.6685 | 15000
0.011302 | 287.9648 | 15000
0.011302 | 294.2611 | 15000
Note on A2: Data group defining the grid variables for the evaporator liquid pressure differential
Note on C2: Data group defining the lookup variables for the evaporator liquid pressure differential
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Pressure difference across the evaporator

## performance_map_cooling
performance.performance_map_cooling
grid_variables | [5 empty] | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_air_entering_drybulb_temperature | condenser_air_entering_relative_humidity | ambient_pressure | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | condenser_air_volumetric_flow_rate | oil_cooler_heat | auxiliary_heat | operation_state
m3/s | K | K | - | Pa | - | W | W | W | m3/s | W | W | -
0.011302 | 275.3722 | 285.9278 | 0.4 | 101325 | 1 | 14192.0286 | 60620.9827 | 74813.0113 | 7.9646 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 285.9278 | 0.4 | 101325 | 2 | 30288.3935 | 121241.9654 | 151530.3589 | 15.9292 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 285.9278 | 0.4 | 101325 | 3 | 48922.2005 | 181862.9481 | 230785.1486 | 23.8939 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 285.9278 | 0.4 | 101325 | 4 | 65032.2031 | 242483.9308 | 307516.1339 | 31.8585 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 299.0019 | 0.4 | 101325 | 1 | 16856.2894 | 60797.1101 | 77653.3995 | 7.9646 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 299.0019 | 0.4 | 101325 | 2 | 35974.415 | 121594.2202 | 157568.6352 | 15.9292 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 299.0019 | 0.4 | 101325 | 3 | 58106.3352 | 182391.3303 | 240497.6655 | 23.8939 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 299.0019 | 0.4 | 101325 | 4 | 77240.6586 | 243188.4404 | 320429.0991 | 31.8585 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 312.0759 | 0.4 | 101325 | 1 | 19149.1806 | 53353.779 | 72502.9596 | 7.9646 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 312.0759 | 0.4 | 101325 | 2 | 40867.8655 | 106707.5581 | 147575.4236 | 15.9292 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 312.0759 | 0.4 | 101325 | 3 | 66010.2989 | 160061.3371 | 226071.6361 | 23.8939 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 312.0759 | 0.4 | 101325 | 4 | 87747.3851 | 213415.1162 | 301162.5012 | 31.8585 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 325.15 | 0.4 | 101325 | 1 | 18344.2606 | 38290.9895 | 56635.25 | 7.9646 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 325.15 | 0.4 | 101325 | 2 | 39150.0185 | 76581.979 | 115731.9974 | 15.9292 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 325.15 | 0.4 | 101325 | 3 | 63235.6104 | 114872.9684 | 178108.5789 | 23.8939 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 325.15 | 0.4 | 101325 | 4 | 84058.9961 | 153163.9579 | 237222.954 | 31.8585 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 285.9278 | 0.4 | 101325 | 1 | 15381.0311 | 75026.4707 | 90407.5018 | 7.9646 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 285.9278 | 0.4 | 101325 | 2 | 32825.943 | 150052.9415 | 182878.8844 | 15.9292 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 285.9278 | 0.4 | 101325 | 3 | 53020.8828 | 225079.4122 | 278100.295 | 23.8939 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 285.9278 | 0.4 | 101325 | 4 | 70480.5749 | 300105.883 | 370586.4579 | 31.8585 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 299.0019 | 0.4 | 101325 | 1 | 17658.4157 | 73861.8458 | 91520.2615 | 7.9646 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 299.0019 | 0.4 | 101325 | 2 | 37686.2997 | 147723.6915 | 185409.9912 | 15.9292 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 299.0019 | 0.4 | 101325 | 3 | 60871.3931 | 221585.5373 | 282456.9304 | 23.8939 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 299.0019 | 0.4 | 101325 | 4 | 80916.2458 | 295447.3831 | 376363.6288 | 31.8585 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 312.0759 | 0.4 | 101325 | 1 | 20281.4788 | 65077.7623 | 85359.2411 | 7.9646 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 312.0759 | 0.4 | 101325 | 2 | 43284.3978 | 130155.5246 | 173439.9224 | 15.9292 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 312.0759 | 0.4 | 101325 | 3 | 69913.5128 | 195233.2869 | 265146.7997 | 23.8939 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 312.0759 | 0.4 | 101325 | 4 | 92935.921 | 260311.0492 | 353246.9702 | 31.8585 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 325.15 | 0.4 | 101325 | 1 | 20576.3968 | 48674.2203 | 69250.6171 | 7.9646 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 325.15 | 0.4 | 101325 | 2 | 43913.8068 | 97348.4407 | 141262.2475 | 15.9292 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 325.15 | 0.4 | 101325 | 3 | 70930.1423 | 146022.661 | 216952.8034 | 23.8939 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 325.15 | 0.4 | 101325 | 4 | 94287.325 | 194696.8814 | 288984.2064 | 31.8585 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 285.9278 | 0.4 | 101325 | 1 | 16656.7239 | 79838.1312 | 96494.8551 | 7.9646 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 285.9278 | 0.4 | 101325 | 2 | 35548.5055 | 159676.2625 | 195224.768 | 15.9292 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 285.9278 | 0.4 | 101325 | 3 | 57418.4006 | 239514.3937 | 296932.7943 | 23.8939 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 285.9278 | 0.4 | 101325 | 4 | 76326.1883 | 319352.525 | 395678.7133 | 31.8585 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 299.0019 | 0.4 | 101325 | 1 | 18066.3444 | 77332.7539 | 95399.0982 | 7.9646 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 299.0019 | 0.4 | 101325 | 2 | 38556.8943 | 154665.5077 | 193222.4021 | 15.9292 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 299.0019 | 0.4 | 101325 | 3 | 62277.5888 | 231998.2616 | 294275.8504 | 23.8939 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 299.0019 | 0.4 | 101325 | 4 | 82785.4994 | 309331.0155 | 392116.5148 | 31.8585 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 312.0759 | 0.4 | 101325 | 1 | 19968.5596 | 67207.918 | 87176.4776 | 7.9646 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 312.0759 | 0.4 | 101325 | 2 | 42616.5707 | 134415.836 | 177032.4067 | 15.9292 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 312.0759 | 0.4 | 101325 | 3 | 68834.8299 | 201623.754 | 270458.5839 | 23.8939 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 312.0759 | 0.4 | 101325 | 4 | 91502.0295 | 268831.672 | 360333.7016 | 31.8585 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 325.15 | 0.4 | 101325 | 1 | 19742.1635 | 49463.6237 | 69205.7872 | 7.9646 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 325.15 | 0.4 | 101325 | 2 | 42133.4 | 98927.2473 | 141060.6473 | 15.9292 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 325.15 | 0.4 | 101325 | 3 | 68054.4064 | 148390.871 | 216445.2774 | 23.8939 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 325.15 | 0.4 | 101325 | 4 | 90464.6138 | 197854.4947 | 288319.1085 | 31.8585 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 285.9278 | 0.4 | 101325 | 1 | 18387.2258 | 75055.9642 | 93443.19 | 7.9646 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 285.9278 | 0.4 | 101325 | 2 | 39241.7141 | 150111.9284 | 189353.6425 | 15.9292 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 285.9278 | 0.4 | 101325 | 3 | 63383.7185 | 225167.8926 | 288551.611 | 23.8939 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 285.9278 | 0.4 | 101325 | 4 | 84255.8758 | 300223.8568 | 384479.7326 | 31.8585 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 299.0019 | 0.4 | 101325 | 1 | 18577.853 | 71209.8344 | 89787.6874 | 7.9646 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 299.0019 | 0.4 | 101325 | 2 | 39648.5476 | 142419.6689 | 182068.2164 | 15.9292 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 299.0019 | 0.4 | 101325 | 3 | 64040.8411 | 213629.5033 | 277670.3443 | 23.8939 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 299.0019 | 0.4 | 101325 | 4 | 85129.3878 | 284839.3377 | 369968.7255 | 31.8585 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 312.0759 | 0.4 | 101325 | 1 | 18837.859 | 59744.2462 | 78582.1052 | 7.9646 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 312.0759 | 0.4 | 101325 | 2 | 40203.4482 | 119488.4923 | 159691.9405 | 15.9292 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 312.0759 | 0.4 | 101325 | 3 | 64937.1236 | 179232.7385 | 244169.8621 | 23.8939 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 312.0759 | 0.4 | 101325 | 4 | 86320.8148 | 238976.9847 | 325297.7995 | 31.8585 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 325.15 | 0.4 | 101325 | 1 | 16598.6557 | 40659.1994 | 57257.8552 | 7.9646 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 325.15 | 0.4 | 101325 | 2 | 35424.5774 | 81318.3989 | 116742.9763 | 15.9292 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 325.15 | 0.4 | 101325 | 3 | 57218.2304 | 121977.5983 | 179195.8287 | 23.8939 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 325.15 | 0.4 | 101325 | 4 | 76060.1024 | 162636.7977 | 238696.9001 | 31.8585 | 0 | 0 | NORMAL
Note on A2: Data group defining the grid variables for cooling performance
Note on G2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Entering condenser air drybulb temperature
Note on D3: Entering condenser air relative humidity
Note on E3: Ambient pressure used to calculate the performance
Note on F3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on G3: Total power input
Note on H3: Refrigeration capacity
Note on I3: Condenser heat rejection
Note on J3: Condenser air flow
Note on K3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on L3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).
Note on M3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation