## RS0001
RS0001: Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 3.0.0 |  | ✓
| description | ASHRAE 90.1-2022 Appendix J curve set 'AA': 150.0-300.0 ton, 5.55 COP, 5.90 IPLV liquid-cooled, centrifugal compressor chiller |  | ✓
| id | 20d3420e-01e1-4a25-9b10-7b07965c0718 |  | ✓
| data_timestamp | 2025-02-18T13:40Z |  | ✓
| data_version | 3 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2022 Appendix J curve set 'AA' for Performance Rating Method (PRM)
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | CENTRIFUGAL
performance |  |  |  | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| cycling_degradation_coefficient | 0 | - | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
performance.performance_map_evaporator_liquid_pressure_differential |  | $performance_map_evaporator_liqu |  | ✓
| condenser_type | LIQUID |  | ✓
performance.condenser_liquid_type
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| condenser_fouling_factor | 0 | m2-K/W
performance.performance_map_condenser_liquid_pressure_differential |  | $performance_map_condenser_liqui
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
performance.scaling
| minimum | 0.66667 | -
| maximum | 1.3333 | -
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on B20: Type of compressor speed control
Note on B21: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A22: Type of liquid in evaporator
Note on A23: An array of all liquid components within the liquid mixture
Note on B24: Defines whether concentration is defined on a volume or mass basis
Note on B25: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on A26: Data group describing the liquid pressure differential through the evaporator
Note on B27: Heat rejection method of the condenser
Note on A28: Type of liquid in condenser
Note on A29: An array of all liquid components within the liquid mixture
Note on B30: Defines whether concentration is defined on a volume or mass basis
Note on B31: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on A32: Data group describing the liquid pressure differential through the condenser
Note on A33: Data group describing cooling performance over a range of conditions
Note on A34: Data group describing standby performance
Note on A35: Specifies the range the performance data can be scaled to represent different capacity equipment
Note on B36: Minimum scaling factor
Note on B37: Maximum scaling factor

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_evaporator_liqu
performance.performance_map_evaporator_liquid_pressure_differential
grid_variables |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | evaporator_liquid_differential_pressure
m3/s | K | Pa
0.033905 | 275.3722 | 15000
0.033905 | 281.6685 | 15000
0.033905 | 287.9648 | 15000
0.033905 | 294.2611 | 15000
Note on A2: Data group defining the grid variables for the evaporator liquid pressure differential
Note on C2: Data group defining the lookup variables for the evaporator liquid pressure differential
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Pressure difference across the evaporator

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_condenser_liqui
performance.performance_map_condenser_liquid_pressure_differential
grid_variables |  | lookup_variables
condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | condenser_liquid_differential_pressure
m3/s | K | Pa
0.043424 | 285.9278 | 15000
0.043424 | 297.0389 | 15000
0.043424 | 308.15 | 15000
0.043424 | 319.2611 | 15000
Note on A2: Data group defining the grid variables for the condenser liquid pressure differential
Note on C2: Data group defining the lookup variables for the condenser liquid pressure differential
Note on A3: Condenser liquid flow
Note on B3: Entering condenser liquid temperature
Note on C3: Pressure difference across the condenser

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | oil_cooler_heat | auxiliary_heat | operation_state
m3/s | K | m3/s | K | - | W | W | W | W | W | -
0.033905 | 275.3722 | 0.043424 | 285.9278 | 1 | 43227.7738 | 187663.795 | 230891.5688 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043424 | 285.9278 | 2 | 57298.6645 | 375327.5899 | 432626.2544 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043424 | 285.9278 | 3 | 79843.2669 | 562991.3849 | 642834.6518 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043424 | 285.9278 | 4 | 110861.5812 | 750655.1798 | 861516.761 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043424 | 297.0389 | 1 | 50578.7995 | 174120.9789 | 224699.7784 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043424 | 297.0389 | 2 | 67042.4916 | 348241.9578 | 415284.4494 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043424 | 297.0389 | 3 | 93420.8781 | 522362.9367 | 615783.8148 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043424 | 297.0389 | 4 | 129713.9591 | 696483.9156 | 826197.8748 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043424 | 308.15 | 1 | 47314.5131 | 152860.6236 | 200175.1367 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043424 | 308.15 | 2 | 62715.661 | 305721.2472 | 368436.9082 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043424 | 308.15 | 3 | 87391.6227 | 458581.8708 | 545973.4935 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043424 | 308.15 | 4 | 121342.398 | 611442.4944 | 732784.8924 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043424 | 319.2611 | 1 | 35614.5479 | 123882.729 | 159497.2769 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043424 | 319.2611 | 2 | 47207.2894 | 247765.4581 | 294972.7475 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043424 | 319.2611 | 3 | 65781.3624 | 371648.1871 | 437429.5495 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043424 | 319.2611 | 4 | 91336.7667 | 495530.9162 | 586867.6829 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043424 | 285.9278 | 1 | 41362.1827 | 216979.9424 | 258342.1251 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043424 | 285.9278 | 2 | 54825.8126 | 433959.8848 | 488785.6975 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043424 | 285.9278 | 3 | 76397.4524 | 650939.8273 | 727337.2797 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043424 | 285.9278 | 4 | 106077.1021 | 867919.7697 | 973996.8718 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043424 | 297.0389 | 1 | 54419.8332 | 212405.1024 | 266824.9356 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043424 | 297.0389 | 2 | 72133.804 | 424810.2048 | 496944.0088 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043424 | 297.0389 | 3 | 100515.4068 | 637215.3071 | 737730.714 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043424 | 297.0389 | 4 | 139564.6417 | 849620.4095 | 989185.0512 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043424 | 308.15 | 1 | 56171.8843 | 200112.7231 | 256284.6074 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043424 | 308.15 | 2 | 74456.1579 | 400225.4461 | 474681.604 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043424 | 308.15 | 3 | 103751.5087 | 600338.1692 | 704089.678 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043424 | 308.15 | 4 | 144057.9369 | 800450.8923 | 944508.8292 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043424 | 319.2611 | 1 | 47566.4385 | 180102.8045 | 227669.243 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043424 | 319.2611 | 2 | 63049.5896 | 360205.609 | 423255.1987 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043424 | 319.2611 | 3 | 87856.9381 | 540308.4135 | 628165.3516 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043424 | 319.2611 | 4 | 121988.4838 | 720411.218 | 842399.7018 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043424 | 285.9278 | 1 | 36247.398 | 216793.1096 | 253040.5076 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043424 | 285.9278 | 2 | 48046.1359 | 433586.2192 | 481632.3551 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043424 | 285.9278 | 3 | 66950.2595 | 650379.3288 | 717329.5883 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043424 | 285.9278 | 4 | 92959.7687 | 867172.4384 | 960132.2071 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043424 | 297.0389 | 1 | 52692.3603 | 221186.2455 | 273878.6058 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043424 | 297.0389 | 2 | 69844.0286 | 442372.4911 | 512216.5197 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043424 | 297.0389 | 3 | 97324.7016 | 663558.7366 | 760883.4382 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043424 | 297.0389 | 4 | 135134.3792 | 884744.9822 | 1019879.3614 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043424 | 308.15 | 1 | 58423.308 | 217861.8422 | 276285.1502 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043424 | 308.15 | 2 | 77440.4329 | 435723.6845 | 513164.1174 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043424 | 308.15 | 3 | 107909.9699 | 653585.5267 | 761495.4966 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043424 | 308.15 | 4 | 149831.9189 | 871447.369 | 1021279.2878 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043424 | 319.2611 | 1 | 53156.813 | 206819.8997 | 259976.7127 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043424 | 319.2611 | 2 | 70459.6634 | 413639.7994 | 484099.4627 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043424 | 319.2611 | 3 | 98182.5626 | 620459.699 | 718642.2616 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043424 | 319.2611 | 4 | 136325.5106 | 827279.5987 | 963605.1093 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043424 | 285.9278 | 1 | 29947.9332 | 187103.2965 | 217051.2296 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043424 | 285.9278 | 2 | 39696.1588 | 374206.5929 | 413902.7517 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043424 | 285.9278 | 3 | 55314.9193 | 561309.8894 | 616624.8087 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043424 | 285.9278 | 4 | 76804.2148 | 748413.1858 | 825217.4006 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043424 | 297.0389 | 1 | 47417.0818 | 200464.4084 | 247881.4902 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043424 | 297.0389 | 2 | 62851.6165 | 400928.8168 | 463780.4333 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043424 | 297.0389 | 3 | 87581.0709 | 601393.2252 | 688974.2961 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043424 | 297.0389 | 4 | 121605.4449 | 801857.6336 | 923463.0785 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043424 | 308.15 | 1 | 56045.673 | 206107.9811 | 262153.6541 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043424 | 308.15 | 2 | 74288.8641 | 412215.9622 | 486504.8263 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043424 | 308.15 | 3 | 103518.3919 | 618323.9433 | 721842.3352 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043424 | 308.15 | 4 | 143734.2565 | 824431.9244 | 968166.181 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043424 | 319.2611 | 1 | 54318.7481 | 204034.0145 | 258352.7626 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043424 | 319.2611 | 2 | 71999.8151 | 408068.0291 | 480067.8442 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043424 | 319.2611 | 3 | 100328.6989 | 612102.0436 | 712430.7425 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043424 | 319.2611 | 4 | 139305.3996 | 816136.0582 | 955441.4577 | 0 | 0 | NORMAL
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on J3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).
Note on K3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation