## RS0001
RS0001: Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 3.0.0 |  | ✓
| description | ASHRAE 90.1-2022 Appendix J curve set 'AB': 300.0+ ton, 6.10 COP, 6.40 IPLV liquid-cooled, centrifugal compressor chiller |  | ✓
| id | f2d6adcc-2224-4280-af0c-0895b9c01fe2 |  | ✓
| data_timestamp | 2025-02-18T13:40Z |  | ✓
| data_version | 3 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2022 Appendix J curve set 'AB' for Performance Rating Method (PRM)
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | CENTRIFUGAL
performance |  |  |  | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| cycling_degradation_coefficient | 0 | - | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
performance.performance_map_evaporator_liquid_pressure_differential |  | $performance_map_evaporator_liqu |  | ✓
| condenser_type | LIQUID |  | ✓
performance.condenser_liquid_type
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| condenser_fouling_factor | 0 | m2-K/W
performance.performance_map_condenser_liquid_pressure_differential |  | $performance_map_condenser_liqui
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
performance.scaling
| minimum | 0.85714 | -
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on B20: Type of compressor speed control
Note on B21: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A22: Type of liquid in evaporator
Note on A23: An array of all liquid components within the liquid mixture
Note on B24: Defines whether concentration is defined on a volume or mass basis
Note on B25: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on A26: Data group describing the liquid pressure differential through the evaporator
Note on B27: Heat rejection method of the condenser
Note on A28: Type of liquid in condenser
Note on A29: An array of all liquid components within the liquid mixture
Note on B30: Defines whether concentration is defined on a volume or mass basis
Note on B31: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on A32: Data group describing the liquid pressure differential through the condenser
Note on A33: Data group describing cooling performance over a range of conditions
Note on A34: Data group describing standby performance
Note on A35: Specifies the range the performance data can be scaled to represent different capacity equipment
Note on B36: Minimum scaling factor

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_evaporator_liqu
performance.performance_map_evaporator_liquid_pressure_differential
grid_variables |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | evaporator_liquid_differential_pressure
m3/s | K | Pa
0.052741 | 275.3722 | 15000
0.052741 | 281.6685 | 15000
0.052741 | 287.9648 | 15000
0.052741 | 294.2611 | 15000
Note on A2: Data group defining the grid variables for the evaporator liquid pressure differential
Note on C2: Data group defining the lookup variables for the evaporator liquid pressure differential
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Pressure difference across the evaporator

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_condenser_liqui
performance.performance_map_condenser_liquid_pressure_differential
grid_variables |  | lookup_variables
condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | condenser_liquid_differential_pressure
m3/s | K | Pa
0.066619 | 285.9278 | 15000
0.066619 | 297.0389 | 15000
0.066619 | 308.15 | 15000
0.066619 | 319.2611 | 15000
Note on A2: Data group defining the grid variables for the condenser liquid pressure differential
Note on C2: Data group defining the lookup variables for the condenser liquid pressure differential
Note on A3: Condenser liquid flow
Note on B3: Entering condenser liquid temperature
Note on C3: Pressure difference across the condenser

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | oil_cooler_heat | auxiliary_heat | operation_state
m3/s | K | m3/s | K | - | W | W | W | W | W | -
0.052741 | 275.3722 | 0.066619 | 285.9278 | 1 | 65692.6105 | 306892.8945 | 372585.505 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.066619 | 285.9278 | 2 | 89615.4908 | 613785.789 | 703401.2798 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.066619 | 285.9278 | 3 | 125079.5763 | 920678.6835 | 1045758.2598 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.066619 | 285.9278 | 4 | 172084.8669 | 1227571.578 | 1399656.4448 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.066619 | 297.0389 | 1 | 74209.8442 | 280834.6937 | 355044.538 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.066619 | 297.0389 | 2 | 101234.394 | 561669.3875 | 662903.7815 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.066619 | 297.0389 | 3 | 141296.499 | 842504.0812 | 983800.5802 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.066619 | 297.0389 | 4 | 194396.1592 | 1123338.7749 | 1317734.9341 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.066619 | 308.15 | 1 | 70094.8065 | 243607.2273 | 313702.0338 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.066619 | 308.15 | 2 | 95620.8079 | 487214.4546 | 582835.2625 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.066619 | 308.15 | 3 | 133461.4141 | 730821.6819 | 864283.096 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.066619 | 308.15 | 4 | 183616.6252 | 974428.9092 | 1158045.5344 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.066619 | 319.2611 | 1 | 55542.4177 | 195210.4952 | 250752.9129 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.066619 | 319.2611 | 2 | 75768.9638 | 390420.9904 | 466189.9542 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.066619 | 319.2611 | 3 | 105753.4786 | 585631.4856 | 691384.9641 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.066619 | 319.2611 | 4 | 145495.962 | 780841.9808 | 926337.9428 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.066619 | 285.9278 | 1 | 61360.4821 | 347400.8874 | 408761.3695 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.066619 | 285.9278 | 2 | 83705.7575 | 694801.7748 | 778507.5322 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.066619 | 285.9278 | 3 | 116831.148 | 1042202.6621 | 1159033.8102 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.066619 | 285.9278 | 4 | 160736.6539 | 1389603.5495 | 1550340.2034 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.066619 | 297.0389 | 1 | 75196.8734 | 332171.3024 | 407368.1758 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.066619 | 297.0389 | 2 | 102580.8637 | 664342.6047 | 766923.4684 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.066619 | 297.0389 | 3 | 143175.8153 | 996513.9071 | 1139689.7224 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.066619 | 297.0389 | 4 | 196981.7283 | 1328685.2095 | 1525666.9378 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.066619 | 308.15 | 1 | 76269.2967 | 305772.4517 | 382041.7484 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.066619 | 308.15 | 2 | 104043.8248 | 611544.9033 | 715588.7282 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.066619 | 308.15 | 3 | 145217.723 | 917317.355 | 1062535.078 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.066619 | 308.15 | 4 | 199790.9912 | 1223089.8067 | 1422880.7979 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.066619 | 319.2611 | 1 | 65919.9458 | 268204.3353 | 334124.2811 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.066619 | 319.2611 | 2 | 89925.6134 | 536408.6706 | 626334.284 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.066619 | 319.2611 | 3 | 125512.4256 | 804613.0059 | 930125.4315 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.066619 | 319.2611 | 4 | 172680.3822 | 1072817.3412 | 1245497.7234 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.066619 | 285.9278 | 1 | 55784.3083 | 350091.2494 | 405875.5577 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.066619 | 285.9278 | 2 | 76098.9421 | 700182.4989 | 776281.441 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.066619 | 285.9278 | 3 | 106214.0412 | 1050273.7483 | 1156487.7895 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.066619 | 285.9278 | 4 | 146129.6056 | 1400364.9977 | 1546494.6033 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.066619 | 297.0389 | 1 | 72130.6592 | 345690.2802 | 417820.9393 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.066619 | 297.0389 | 2 | 98398.0447 | 691380.5603 | 789778.605 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.066619 | 297.0389 | 3 | 137337.7039 | 1037070.8405 | 1174408.5443 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.066619 | 297.0389 | 4 | 188949.6366 | 1382761.1206 | 1571710.7572 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.066619 | 308.15 | 1 | 76347.1397 | 330120.0452 | 406467.1849 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.066619 | 308.15 | 2 | 104150.0154 | 660240.0904 | 764390.1058 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.066619 | 308.15 | 3 | 145365.9371 | 990360.1356 | 1135726.0727 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.066619 | 308.15 | 4 | 199994.9047 | 1320480.1808 | 1520475.0854 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.066619 | 319.2611 | 1 | 68923.2171 | 303380.5446 | 372303.7616 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.066619 | 319.2611 | 2 | 94022.5679 | 606761.0891 | 700783.657 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.066619 | 319.2611 | 3 | 131230.6928 | 910141.6337 | 1041372.3265 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.066619 | 319.2611 | 4 | 180547.592 | 1213522.1783 | 1394069.7703 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.066619 | 285.9278 | 1 | 51087.7242 | 314963.9806 | 366051.7048 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.066619 | 285.9278 | 2 | 69692.0315 | 629927.9613 | 699619.9928 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.066619 | 285.9278 | 3 | 97271.6847 | 944891.9419 | 1042163.6266 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.066619 | 285.9278 | 4 | 133826.6839 | 1259855.9225 | 1393682.6064 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.066619 | 297.0389 | 1 | 67838.9246 | 321391.6271 | 389230.5517 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.066619 | 297.0389 | 2 | 92543.4151 | 642783.2542 | 735326.6693 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.066619 | 297.0389 | 3 | 129166.186 | 964174.8813 | 1093341.0672 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.066619 | 297.0389 | 4 | 177707.2371 | 1285566.5084 | 1463273.7454 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.066619 | 308.15 | 1 | 73860.1466 | 316650.0079 | 390510.1544 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.066619 | 308.15 | 2 | 100757.3491 | 633300.0158 | 734057.3648 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.066619 | 308.15 | 3 | 140630.6701 | 949950.0236 | 1090580.6937 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.066619 | 308.15 | 4 | 193480.1097 | 1266600.0315 | 1460080.1412 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.066619 | 319.2611 | 1 | 68788.1307 | 300739.123 | 369527.2537 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.066619 | 319.2611 | 2 | 93838.2879 | 601478.246 | 695316.5338 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.066619 | 319.2611 | 3 | 130973.4866 | 902217.3689 | 1033190.8555 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.066619 | 319.2611 | 4 | 180193.7268 | 1202956.4919 | 1383150.2187 | 0 | 0 | NORMAL
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on J3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).
Note on K3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation