## RS0001
RS0001: Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 3.0.0 |  | ✓
| description | ASHRAE 90.1-2022 Appendix J curve set 'B': 150.0+ ton, 2.96 COP, 4.10 IPLV air-cooled, compressor chiller |  | ✓
| id | 4ff49d43-9c23-46ff-aae2-6cf3f14ffa8c |  | ✓
| data_timestamp | 2025-02-18T13:40Z |  | ✓
| data_version | 3 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2022 Appendix J curve set 'B' for Energy Cost Budget (ECB) Path A
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
performance |  |  |  | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| cycling_degradation_coefficient | 0 | - | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
performance.performance_map_evaporator_liquid_pressure_differential |  | $performance_map_evaporator_liqu |  | ✓
| condenser_type | AIR |  | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
performance.scaling
| minimum | 0.75 | -
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on A18: Data group containing performance information
Note on B19: Type of compressor speed control
Note on B20: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A21: Type of liquid in evaporator
Note on A22: An array of all liquid components within the liquid mixture
Note on B23: Defines whether concentration is defined on a volume or mass basis
Note on B24: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on A25: Data group describing the liquid pressure differential through the evaporator
Note on B26: Heat rejection method of the condenser
Note on A27: Data group describing cooling performance over a range of conditions
Note on A28: Data group describing standby performance
Note on A29: Specifies the range the performance data can be scaled to represent different capacity equipment
Note on B30: Minimum scaling factor

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_evaporator_liqu
performance.performance_map_evaporator_liquid_pressure_differential
grid_variables |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | evaporator_liquid_differential_pressure
m3/s | K | Pa
0.030137 | 275.3722 | 15000
0.030137 | 281.6685 | 15000
0.030137 | 287.9648 | 15000
0.030137 | 294.2611 | 15000
Note on A2: Data group defining the grid variables for the evaporator liquid pressure differential
Note on C2: Data group defining the lookup variables for the evaporator liquid pressure differential
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Pressure difference across the evaporator

## performance_map_cooling
performance.performance_map_cooling
grid_variables | [5 empty] | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_air_entering_drybulb_temperature | condenser_air_entering_relative_humidity | ambient_pressure | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | condenser_air_volumetric_flow_rate | oil_cooler_heat | auxiliary_heat | operation_state
m3/s | K | K | - | Pa | - | W | W | W | m3/s | W | W | -
0.030137 | 275.3722 | 285.9278 | 0.4 | 101325 | 1 | 40328.768 | 167873.4879 | 208202.2558 | 21.2332 | 0 | 0 | NORMAL
0.030137 | 275.3722 | 285.9278 | 0.4 | 101325 | 2 | 81327.2569 | 335746.9757 | 417074.2327 | 42.4664 | 0 | 0 | NORMAL
0.030137 | 275.3722 | 285.9278 | 0.4 | 101325 | 3 | 130623.29 | 503620.4636 | 634243.7536 | 63.6996 | 0 | 0 | NORMAL
0.030137 | 275.3722 | 285.9278 | 0.4 | 101325 | 4 | 175204.7401 | 671493.9515 | 846698.6916 | 84.9328 | 0 | 0 | NORMAL
0.030137 | 275.3722 | 299.0019 | 0.4 | 101325 | 1 | 46488.9911 | 160861.9393 | 207350.9304 | 21.2332 | 0 | 0 | NORMAL
0.030137 | 275.3722 | 299.0019 | 0.4 | 101325 | 2 | 93750.0031 | 321723.8786 | 415473.8817 | 42.4664 | 0 | 0 | NORMAL
0.030137 | 275.3722 | 299.0019 | 0.4 | 101325 | 3 | 150576.0099 | 482585.8179 | 633161.8278 | 63.6996 | 0 | 0 | NORMAL
0.030137 | 275.3722 | 299.0019 | 0.4 | 101325 | 4 | 201967.2807 | 643447.7572 | 845415.0379 | 84.9328 | 0 | 0 | NORMAL
0.030137 | 275.3722 | 312.0759 | 0.4 | 101325 | 1 | 53273.1668 | 140084.2685 | 193357.4353 | 21.2332 | 0 | 0 | NORMAL
0.030137 | 275.3722 | 312.0759 | 0.4 | 101325 | 2 | 107431.0161 | 280168.537 | 387599.5531 | 42.4664 | 0 | 0 | NORMAL
0.030137 | 275.3722 | 312.0759 | 0.4 | 101325 | 3 | 172549.6876 | 420252.8055 | 592802.4931 | 63.6996 | 0 | 0 | NORMAL
0.030137 | 275.3722 | 312.0759 | 0.4 | 101325 | 4 | 231440.5277 | 560337.074 | 791777.6017 | 84.9328 | 0 | 0 | NORMAL
0.030137 | 275.3722 | 325.15 | 0.4 | 101325 | 1 | 54260.0766 | 105540.4755 | 159800.5521 | 21.2332 | 0 | 0 | NORMAL
0.030137 | 275.3722 | 325.15 | 0.4 | 101325 | 2 | 109421.225 | 211080.9509 | 320502.1759 | 42.4664 | 0 | 0 | NORMAL
0.030137 | 275.3722 | 325.15 | 0.4 | 101325 | 3 | 175746.2497 | 316621.4264 | 492367.6761 | 63.6996 | 0 | 0 | NORMAL
0.030137 | 275.3722 | 325.15 | 0.4 | 101325 | 4 | 235728.0696 | 422161.9018 | 657889.9715 | 84.9328 | 0 | 0 | NORMAL
0.030137 | 281.6685 | 285.9278 | 0.4 | 101325 | 1 | 42760.0036 | 207960.7096 | 250720.7133 | 21.2332 | 0 | 0 | NORMAL
0.030137 | 281.6685 | 285.9278 | 0.4 | 101325 | 2 | 86230.1026 | 415921.4193 | 502151.5219 | 42.4664 | 0 | 0 | NORMAL
0.030137 | 281.6685 | 285.9278 | 0.4 | 101325 | 3 | 138497.9665 | 623882.1289 | 762380.0954 | 63.6996 | 0 | 0 | NORMAL
0.030137 | 281.6685 | 285.9278 | 0.4 | 101325 | 4 | 185767.0268 | 831842.8386 | 1017609.8654 | 84.9328 | 0 | 0 | NORMAL
0.030137 | 281.6685 | 299.0019 | 0.4 | 101325 | 1 | 49029.1401 | 198300.2252 | 247329.3653 | 21.2332 | 0 | 0 | NORMAL
0.030137 | 281.6685 | 299.0019 | 0.4 | 101325 | 2 | 98872.4842 | 396600.4504 | 495472.9346 | 42.4664 | 0 | 0 | NORMAL
0.030137 | 281.6685 | 299.0019 | 0.4 | 101325 | 3 | 158803.4525 | 594900.6755 | 753704.128 | 63.6996 | 0 | 0 | NORMAL
0.030137 | 281.6685 | 299.0019 | 0.4 | 101325 | 4 | 213002.7319 | 793200.9007 | 1006203.6326 | 84.9328 | 0 | 0 | NORMAL
0.030137 | 281.6685 | 312.0759 | 0.4 | 101325 | 1 | 57954.2424 | 174873.6185 | 232827.8609 | 21.2332 | 0 | 0 | NORMAL
0.030137 | 281.6685 | 312.0759 | 0.4 | 101325 | 2 | 116870.9039 | 349747.2369 | 466618.1408 | 42.4664 | 0 | 0 | NORMAL
0.030137 | 281.6685 | 312.0759 | 0.4 | 101325 | 3 | 187711.5072 | 524620.8554 | 712332.3626 | 63.6996 | 0 | 0 | NORMAL
0.030137 | 281.6685 | 312.0759 | 0.4 | 101325 | 4 | 251777.044 | 699494.4739 | 951271.5179 | 84.9328 | 0 | 0 | NORMAL
0.030137 | 281.6685 | 325.15 | 0.4 | 101325 | 1 | 63070.7921 | 137680.8895 | 200751.6816 | 21.2332 | 0 | 0 | NORMAL
0.030137 | 281.6685 | 325.15 | 0.4 | 101325 | 2 | 127188.9713 | 275361.7791 | 402550.7504 | 42.4664 | 0 | 0 | NORMAL
0.030137 | 281.6685 | 325.15 | 0.4 | 101325 | 3 | 204283.8098 | 413042.6686 | 617326.4784 | 63.6996 | 0 | 0 | NORMAL
0.030137 | 281.6685 | 325.15 | 0.4 | 101325 | 4 | 274005.4381 | 550723.5581 | 824728.9962 | 84.9328 | 0 | 0 | NORMAL
0.030137 | 287.9648 | 285.9278 | 0.4 | 101325 | 1 | 45389.8819 | 219940.8922 | 265330.7741 | 21.2332 | 0 | 0 | NORMAL
0.030137 | 287.9648 | 285.9278 | 0.4 | 101325 | 2 | 91533.5323 | 439881.7845 | 531415.3168 | 42.4664 | 0 | 0 | NORMAL
0.030137 | 287.9648 | 285.9278 | 0.4 | 101325 | 3 | 147016.0385 | 659822.6767 | 806838.7152 | 63.6996 | 0 | 0 | NORMAL
0.030137 | 287.9648 | 285.9278 | 0.4 | 101325 | 4 | 197192.2987 | 879763.5689 | 1076955.8676 | 84.9328 | 0 | 0 | NORMAL
0.030137 | 287.9648 | 299.0019 | 0.4 | 101325 | 1 | 50012.058 | 207631.4719 | 257643.5299 | 21.2332 | 0 | 0 | NORMAL
0.030137 | 287.9648 | 299.0019 | 0.4 | 101325 | 2 | 100854.6429 | 415262.9437 | 516117.5866 | 42.4664 | 0 | 0 | NORMAL
0.030137 | 287.9648 | 299.0019 | 0.4 | 101325 | 3 | 161987.0849 | 622894.4156 | 784881.5005 | 63.6996 | 0 | 0 | NORMAL
0.030137 | 287.9648 | 299.0019 | 0.4 | 101325 | 4 | 217272.9312 | 830525.8875 | 1047798.8187 | 84.9328 | 0 | 0 | NORMAL
0.030137 | 287.9648 | 312.0759 | 0.4 | 101325 | 1 | 57715.5013 | 181555.9293 | 239271.4305 | 21.2332 | 0 | 0 | NORMAL
0.030137 | 287.9648 | 312.0759 | 0.4 | 101325 | 2 | 116389.4569 | 363111.8585 | 479501.3154 | 42.4664 | 0 | 0 | NORMAL
0.030137 | 287.9648 | 312.0759 | 0.4 | 101325 | 3 | 186938.2339 | 544667.7878 | 731606.0217 | 63.6996 | 0 | 0 | NORMAL
0.030137 | 287.9648 | 312.0759 | 0.4 | 101325 | 4 | 250739.8542 | 726223.717 | 976963.5713 | 84.9328 | 0 | 0 | NORMAL
0.030137 | 287.9648 | 325.15 | 0.4 | 101325 | 1 | 61992.3929 | 141714.2644 | 203706.6574 | 21.2332 | 0 | 0 | NORMAL
0.030137 | 287.9648 | 325.15 | 0.4 | 101325 | 2 | 125014.2646 | 283428.5288 | 408442.7934 | 42.4664 | 0 | 0 | NORMAL
0.030137 | 287.9648 | 325.15 | 0.4 | 101325 | 3 | 200790.9175 | 425142.7932 | 625933.7108 | 63.6996 | 0 | 0 | NORMAL
0.030137 | 287.9648 | 325.15 | 0.4 | 101325 | 4 | 269320.4291 | 566857.0577 | 836177.4868 | 84.9328 | 0 | 0 | NORMAL
0.030137 | 294.2611 | 285.9278 | 0.4 | 101325 | 1 | 49425.929 | 203814.0356 | 253239.9646 | 21.2332 | 0 | 0 | NORMAL
0.030137 | 294.2611 | 285.9278 | 0.4 | 101325 | 2 | 99672.6512 | 407628.0713 | 507300.7225 | 42.4664 | 0 | 0 | NORMAL
0.030137 | 294.2611 | 285.9278 | 0.4 | 101325 | 3 | 160088.6359 | 611442.1069 | 771530.7428 | 63.6996 | 0 | 0 | NORMAL
0.030137 | 294.2611 | 285.9278 | 0.4 | 101325 | 4 | 214726.5457 | 815256.1425 | 1029982.6882 | 84.9328 | 0 | 0 | NORMAL
0.030137 | 294.2611 | 299.0019 | 0.4 | 101325 | 1 | 50965.7852 | 188855.6794 | 239821.4646 | 21.2332 | 0 | 0 | NORMAL
0.030137 | 294.2611 | 299.0019 | 0.4 | 101325 | 2 | 102777.9355 | 377711.3587 | 480489.2942 | 42.4664 | 0 | 0 | NORMAL
0.030137 | 294.2611 | 299.0019 | 0.4 | 101325 | 3 | 165076.1697 | 566567.0381 | 731643.2078 | 63.6996 | 0 | 0 | NORMAL
0.030137 | 294.2611 | 299.0019 | 0.4 | 101325 | 4 | 221416.3142 | 755422.7175 | 976839.0316 | 84.9328 | 0 | 0 | NORMAL
0.030137 | 294.2611 | 312.0759 | 0.4 | 101325 | 1 | 54405.4979 | 160131.2009 | 214536.6988 | 21.2332 | 0 | 0 | NORMAL
0.030137 | 294.2611 | 312.0759 | 0.4 | 101325 | 2 | 109714.4824 | 320262.4017 | 429976.8842 | 42.4664 | 0 | 0 | NORMAL
0.030137 | 294.2611 | 312.0759 | 0.4 | 101325 | 3 | 176217.2634 | 480393.6026 | 656610.866 | 63.6996 | 0 | 0 | NORMAL
0.030137 | 294.2611 | 312.0759 | 0.4 | 101325 | 4 | 236359.8393 | 640524.8035 | 876884.6428 | 84.9328 | 0 | 0 | NORMAL
0.030137 | 294.2611 | 325.15 | 0.4 | 101325 | 1 | 53193.9481 | 117640.6001 | 170834.5482 | 21.2332 | 0 | 0 | NORMAL
0.030137 | 294.2611 | 325.15 | 0.4 | 101325 | 2 | 107271.2632 | 235281.2002 | 342552.4634 | 42.4664 | 0 | 0 | NORMAL
0.030137 | 294.2611 | 325.15 | 0.4 | 101325 | 3 | 172293.1013 | 352921.8004 | 525214.9017 | 63.6996 | 0 | 0 | NORMAL
0.030137 | 294.2611 | 325.15 | 0.4 | 101325 | 4 | 231096.3691 | 470562.4005 | 701658.7696 | 84.9328 | 0 | 0 | NORMAL
Note on A2: Data group defining the grid variables for cooling performance
Note on G2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Entering condenser air drybulb temperature
Note on D3: Entering condenser air relative humidity
Note on E3: Ambient pressure used to calculate the performance
Note on F3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on G3: Total power input
Note on H3: Refrigeration capacity
Note on I3: Condenser heat rejection
Note on J3: Condenser air flow
Note on K3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on L3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).
Note on M3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation