## RS0001
RS0001: Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 3.0.0 |  | ✓
| description | ASHRAE 90.1-2022 Appendix J curve set 'C': 0.0-75.0 ton, 4.69 COP, 5.86 IPLV liquid-cooled, positive displacement compressor chiller |  | ✓
| id | 4ae862fe-bdee-479b-ac94-ff34ee0dfa46 |  | ✓
| data_timestamp | 2025-02-18T13:40Z |  | ✓
| data_version | 3 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2022 Appendix J curve set 'C' for Energy Cost Budget (ECB) Path A
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | SCROLL
performance |  |  |  | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| cycling_degradation_coefficient | 0 | - | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
performance.performance_map_evaporator_liquid_pressure_differential |  | $performance_map_evaporator_liqu |  | ✓
| condenser_type | LIQUID |  | ✓
performance.condenser_liquid_type
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| condenser_fouling_factor | 0 | m2-K/W
performance.performance_map_condenser_liquid_pressure_differential |  | $performance_map_condenser_liqui
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
performance.scaling
| maximum | 2 | -
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on B20: Type of compressor speed control
Note on B21: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A22: Type of liquid in evaporator
Note on A23: An array of all liquid components within the liquid mixture
Note on B24: Defines whether concentration is defined on a volume or mass basis
Note on B25: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on A26: Data group describing the liquid pressure differential through the evaporator
Note on B27: Heat rejection method of the condenser
Note on A28: Type of liquid in condenser
Note on A29: An array of all liquid components within the liquid mixture
Note on B30: Defines whether concentration is defined on a volume or mass basis
Note on B31: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on A32: Data group describing the liquid pressure differential through the condenser
Note on A33: Data group describing cooling performance over a range of conditions
Note on A34: Data group describing standby performance
Note on A35: Specifies the range the performance data can be scaled to represent different capacity equipment
Note on B36: Maximum scaling factor

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_evaporator_liqu
performance.performance_map_evaporator_liquid_pressure_differential
grid_variables |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | evaporator_liquid_differential_pressure
m3/s | K | Pa
0.0056508 | 275.3722 | 15000
0.0056508 | 281.6685 | 15000
0.0056508 | 287.9648 | 15000
0.0056508 | 294.2611 | 15000
Note on A2: Data group defining the grid variables for the evaporator liquid pressure differential
Note on C2: Data group defining the lookup variables for the evaporator liquid pressure differential
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Pressure difference across the evaporator

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_condenser_liqui
performance.performance_map_condenser_liquid_pressure_differential
grid_variables |  | lookup_variables
condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | condenser_liquid_differential_pressure
m3/s | K | Pa
0.0074401 | 285.9278 | 15000
0.0074401 | 297.0389 | 15000
0.0074401 | 308.15 | 15000
0.0074401 | 319.2611 | 15000
Note on A2: Data group defining the grid variables for the condenser liquid pressure differential
Note on C2: Data group defining the lookup variables for the condenser liquid pressure differential
Note on A3: Condenser liquid flow
Note on B3: Entering condenser liquid temperature
Note on C3: Pressure difference across the condenser

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | oil_cooler_heat | auxiliary_heat | operation_state
m3/s | K | m3/s | K | - | W | W | W | W | W | -
0.0056508 | 275.3722 | 0.0074401 | 285.9278 | 1 | 6902.843 | 30884.4837 | 37787.3267 | 0 | 0 | NORMAL
0.0056508 | 275.3722 | 0.0074401 | 285.9278 | 2 | 10149.6476 | 61768.9675 | 71918.6151 | 0 | 0 | NORMAL
0.0056508 | 275.3722 | 0.0074401 | 285.9278 | 3 | 14967.7187 | 92653.4512 | 107621.1699 | 0 | 0 | NORMAL
0.0056508 | 275.3722 | 0.0074401 | 285.9278 | 4 | 21357.0561 | 123537.9349 | 144894.9911 | 0 | 0 | NORMAL
0.0056508 | 275.3722 | 0.0074401 | 297.0389 | 1 | 7874.4996 | 28840.5977 | 36715.0973 | 0 | 0 | NORMAL
0.0056508 | 275.3722 | 0.0074401 | 297.0389 | 2 | 11578.3304 | 57681.1953 | 69259.5257 | 0 | 0 | NORMAL
0.0056508 | 275.3722 | 0.0074401 | 297.0389 | 3 | 17074.6018 | 86521.793 | 103596.3948 | 0 | 0 | NORMAL
0.0056508 | 275.3722 | 0.0074401 | 297.0389 | 4 | 24363.3139 | 115362.3907 | 139725.7046 | 0 | 0 | NORMAL
0.0056508 | 275.3722 | 0.0074401 | 308.15 | 1 | 9119.8224 | 25372.0604 | 34491.8827 | 0 | 0 | NORMAL
0.0056508 | 275.3722 | 0.0074401 | 308.15 | 2 | 13409.4001 | 50744.1207 | 64153.5208 | 0 | 0 | NORMAL
0.0056508 | 275.3722 | 0.0074401 | 308.15 | 3 | 19774.8863 | 76116.1811 | 95891.0674 | 0 | 0 | NORMAL
0.0056508 | 275.3722 | 0.0074401 | 308.15 | 4 | 28216.2811 | 101488.2415 | 129704.5225 | 0 | 0 | NORMAL
0.0056508 | 275.3722 | 0.0074401 | 319.2611 | 1 | 9885.7657 | 20478.8718 | 30364.6376 | 0 | 0 | NORMAL
0.0056508 | 275.3722 | 0.0074401 | 319.2611 | 2 | 14535.6108 | 40957.7436 | 55493.3544 | 0 | 0 | NORMAL
0.0056508 | 275.3722 | 0.0074401 | 319.2611 | 3 | 21435.7129 | 61436.6155 | 82872.3284 | 0 | 0 | NORMAL
0.0056508 | 275.3722 | 0.0074401 | 319.2611 | 4 | 30586.0722 | 81915.4873 | 112501.5595 | 0 | 0 | NORMAL
0.0056508 | 281.6685 | 0.0074401 | 285.9278 | 1 | 7140.9863 | 38055.0049 | 45195.9912 | 0 | 0 | NORMAL
0.0056508 | 281.6685 | 0.0074401 | 285.9278 | 2 | 10499.8035 | 76110.0097 | 86609.8132 | 0 | 0 | NORMAL
0.0056508 | 281.6685 | 0.0074401 | 285.9278 | 3 | 15484.0947 | 114165.0146 | 129649.1093 | 0 | 0 | NORMAL
0.0056508 | 281.6685 | 0.0074401 | 285.9278 | 4 | 22093.8599 | 152220.0195 | 174313.8794 | 0 | 0 | NORMAL
0.0056508 | 281.6685 | 0.0074401 | 297.0389 | 1 | 8270.1519 | 36057.2504 | 44327.4023 | 0 | 0 | NORMAL
0.0056508 | 281.6685 | 0.0074401 | 297.0389 | 2 | 12160.0807 | 72114.5007 | 84274.5814 | 0 | 0 | NORMAL
0.0056508 | 281.6685 | 0.0074401 | 297.0389 | 3 | 17932.5109 | 108171.7511 | 126104.262 | 0 | 0 | NORMAL
0.0056508 | 281.6685 | 0.0074401 | 297.0389 | 4 | 25587.4426 | 144229.0014 | 169816.444 | 0 | 0 | NORMAL
0.0056508 | 281.6685 | 0.0074401 | 308.15 | 1 | 10049.9832 | 32634.8446 | 42684.8278 | 0 | 0 | NORMAL
0.0056508 | 281.6685 | 0.0074401 | 308.15 | 2 | 14777.0692 | 65269.6892 | 80046.7584 | 0 | 0 | NORMAL
0.0056508 | 281.6685 | 0.0074401 | 308.15 | 3 | 21791.7925 | 97904.5338 | 119696.3263 | 0 | 0 | NORMAL
0.0056508 | 281.6685 | 0.0074401 | 308.15 | 4 | 31094.153 | 130539.3785 | 161633.5315 | 0 | 0 | NORMAL
0.0056508 | 281.6685 | 0.0074401 | 319.2611 | 1 | 11765.9499 | 27787.7876 | 39553.7375 | 0 | 0 | NORMAL
0.0056508 | 281.6685 | 0.0074401 | 319.2611 | 2 | 17300.1538 | 55575.5753 | 72875.729 | 0 | 0 | NORMAL
0.0056508 | 281.6685 | 0.0074401 | 319.2611 | 3 | 25512.5935 | 83363.3629 | 108875.9565 | 0 | 0 | NORMAL
0.0056508 | 281.6685 | 0.0074401 | 319.2611 | 4 | 36403.2692 | 111151.1506 | 147554.4198 | 0 | 0 | NORMAL
0.0056508 | 287.9648 | 0.0074401 | 285.9278 | 1 | 7379.6602 | 39691.4298 | 47071.09 | 0 | 0 | NORMAL
0.0056508 | 287.9648 | 0.0074401 | 285.9278 | 2 | 10850.7394 | 79382.8596 | 90233.599 | 0 | 0 | NORMAL
0.0056508 | 287.9648 | 0.0074401 | 285.9278 | 3 | 16001.621 | 119074.2895 | 135075.9105 | 0 | 0 | NORMAL
0.0056508 | 287.9648 | 0.0074401 | 285.9278 | 4 | 22832.305 | 158765.7193 | 181598.0243 | 0 | 0 | NORMAL
0.0056508 | 287.9648 | 0.0074401 | 297.0389 | 1 | 8296.0016 | 37739.8069 | 46035.8085 | 0 | 0 | NORMAL
0.0056508 | 287.9648 | 0.0074401 | 297.0389 | 2 | 12198.089 | 75479.6138 | 87677.7027 | 0 | 0 | NORMAL
0.0056508 | 287.9648 | 0.0074401 | 297.0389 | 3 | 17988.5618 | 113219.4206 | 131207.9825 | 0 | 0 | NORMAL
0.0056508 | 287.9648 | 0.0074401 | 297.0389 | 4 | 25667.4202 | 150959.2275 | 176626.6477 | 0 | 0 | NORMAL
0.0056508 | 287.9648 | 0.0074401 | 308.15 | 1 | 9985.8508 | 34363.5327 | 44349.3835 | 0 | 0 | NORMAL
0.0056508 | 287.9648 | 0.0074401 | 308.15 | 2 | 14682.7716 | 68727.0654 | 83409.837 | 0 | 0 | NORMAL
0.0056508 | 287.9648 | 0.0074401 | 308.15 | 3 | 21652.7314 | 103090.5981 | 124743.3295 | 0 | 0 | NORMAL
0.0056508 | 287.9648 | 0.0074401 | 308.15 | 4 | 30895.7303 | 137454.1308 | 168349.8612 | 0 | 0 | NORMAL
0.0056508 | 287.9648 | 0.0074401 | 319.2611 | 1 | 11773.1924 | 29562.6073 | 41335.7996 | 0 | 0 | NORMAL
0.0056508 | 287.9648 | 0.0074401 | 319.2611 | 2 | 17310.8028 | 59125.2146 | 76436.0174 | 0 | 0 | NORMAL
0.0056508 | 287.9648 | 0.0074401 | 319.2611 | 3 | 25528.2978 | 88687.8219 | 114216.1196 | 0 | 0 | NORMAL
0.0056508 | 287.9648 | 0.0074401 | 319.2611 | 4 | 36425.6771 | 118250.4292 | 154676.1063 | 0 | 0 | NORMAL
0.0056508 | 294.2611 | 0.0074401 | 285.9278 | 1 | 7815.0425 | 35793.7586 | 43608.8012 | 0 | 0 | NORMAL
0.0056508 | 294.2611 | 0.0074401 | 285.9278 | 2 | 11490.9072 | 71587.5172 | 83078.4244 | 0 | 0 | NORMAL
0.0056508 | 294.2611 | 0.0074401 | 285.9278 | 3 | 16945.6785 | 107381.2759 | 124326.9544 | 0 | 0 | NORMAL
0.0056508 | 294.2611 | 0.0074401 | 285.9278 | 4 | 24179.3566 | 143175.0345 | 167354.3911 | 0 | 0 | NORMAL
0.0056508 | 294.2611 | 0.0074401 | 297.0389 | 1 | 8282.7375 | 33888.2672 | 42171.0047 | 0 | 0 | NORMAL
0.0056508 | 294.2611 | 0.0074401 | 297.0389 | 2 | 12178.586 | 67776.5345 | 79955.1205 | 0 | 0 | NORMAL
0.0056508 | 294.2611 | 0.0074401 | 297.0389 | 3 | 17959.8007 | 101664.8017 | 119624.6024 | 0 | 0 | NORMAL
0.0056508 | 294.2611 | 0.0074401 | 297.0389 | 4 | 25626.3817 | 135553.069 | 161179.4507 | 0 | 0 | NORMAL
0.0056508 | 294.2611 | 0.0074401 | 308.15 | 1 | 9392.6246 | 30558.1246 | 39950.7493 | 0 | 0 | NORMAL
0.0056508 | 294.2611 | 0.0074401 | 308.15 | 2 | 13810.517 | 61116.2493 | 74926.7663 | 0 | 0 | NORMAL
0.0056508 | 294.2611 | 0.0074401 | 308.15 | 3 | 20366.4148 | 91674.3739 | 112040.7887 | 0 | 0 | NORMAL
0.0056508 | 294.2611 | 0.0074401 | 308.15 | 4 | 29060.3179 | 122232.4985 | 151292.8165 | 0 | 0 | NORMAL
0.0056508 | 294.2611 | 0.0074401 | 319.2611 | 1 | 10507.2037 | 25803.3308 | 36310.5345 | 0 | 0 | NORMAL
0.0056508 | 294.2611 | 0.0074401 | 319.2611 | 2 | 15449.3468 | 51606.6616 | 67056.0084 | 0 | 0 | NORMAL
0.0056508 | 294.2611 | 0.0074401 | 319.2611 | 3 | 22783.2025 | 77409.9924 | 100193.1948 | 0 | 0 | NORMAL
0.0056508 | 294.2611 | 0.0074401 | 319.2611 | 4 | 32508.7706 | 103213.3231 | 135722.0938 | 0 | 0 | NORMAL
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on J3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).
Note on K3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation