## RS0001
RS0001: Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 3.0.0 |  | ✓
| description | ASHRAE 90.1-2022 Appendix J curve set 'D': 75.0-150.0 ton, 4.88 COP, 6.28 IPLV liquid-cooled, positive displacement compressor chiller |  | ✓
| id | 486dd8c3-9d03-4579-8edd-8f267ef48aad |  | ✓
| data_timestamp | 2025-02-18T13:40Z |  | ✓
| data_version | 3 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2022 Appendix J curve set 'D' for Energy Cost Budget (ECB) Path A
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | SCROLL
performance |  |  |  | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| cycling_degradation_coefficient | 0 | - | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
performance.performance_map_evaporator_liquid_pressure_differential |  | $performance_map_evaporator_liqu |  | ✓
| condenser_type | LIQUID |  | ✓
performance.condenser_liquid_type
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| condenser_fouling_factor | 0 | m2-K/W
performance.performance_map_condenser_liquid_pressure_differential |  | $performance_map_condenser_liqui
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
performance.scaling
| minimum | 0.66667 | -
| maximum | 1.3333 | -
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on B20: Type of compressor speed control
Note on B21: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A22: Type of liquid in evaporator
Note on A23: An array of all liquid components within the liquid mixture
Note on B24: Defines whether concentration is defined on a volume or mass basis
Note on B25: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on A26: Data group describing the liquid pressure differential through the evaporator
Note on B27: Heat rejection method of the condenser
Note on A28: Type of liquid in condenser
Note on A29: An array of all liquid components within the liquid mixture
Note on B30: Defines whether concentration is defined on a volume or mass basis
Note on B31: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on A32: Data group describing the liquid pressure differential through the condenser
Note on A33: Data group describing cooling performance over a range of conditions
Note on A34: Data group describing standby performance
Note on A35: Specifies the range the performance data can be scaled to represent different capacity equipment
Note on B36: Minimum scaling factor
Note on B37: Maximum scaling factor

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_evaporator_liqu
performance.performance_map_evaporator_liquid_pressure_differential
grid_variables |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | evaporator_liquid_differential_pressure
m3/s | K | Pa
0.016952 | 275.3722 | 15000
0.016952 | 281.6685 | 15000
0.016952 | 287.9648 | 15000
0.016952 | 294.2611 | 15000
Note on A2: Data group defining the grid variables for the evaporator liquid pressure differential
Note on C2: Data group defining the lookup variables for the evaporator liquid pressure differential
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Pressure difference across the evaporator

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_condenser_liqui
performance.performance_map_condenser_liquid_pressure_differential
grid_variables |  | lookup_variables
condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | condenser_liquid_differential_pressure
m3/s | K | Pa
0.022163 | 285.9278 | 15000
0.022163 | 297.0389 | 15000
0.022163 | 308.15 | 15000
0.022163 | 319.2611 | 15000
Note on A2: Data group defining the grid variables for the condenser liquid pressure differential
Note on C2: Data group defining the lookup variables for the condenser liquid pressure differential
Note on A3: Condenser liquid flow
Note on B3: Entering condenser liquid temperature
Note on C3: Pressure difference across the condenser

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | oil_cooler_heat | auxiliary_heat | operation_state
m3/s | K | m3/s | K | - | W | W | W | W | W | -
0.016952 | 275.3722 | 0.022163 | 285.9278 | 1 | 17993.8534 | 93056.6902 | 111050.5436 | 0 | 0 | NORMAL
0.016952 | 275.3722 | 0.022163 | 285.9278 | 2 | 27664.7952 | 186113.3804 | 213778.1756 | 0 | 0 | NORMAL
0.016952 | 275.3722 | 0.022163 | 285.9278 | 3 | 41544.3437 | 279170.0706 | 320714.4143 | 0 | 0 | NORMAL
0.016952 | 275.3722 | 0.022163 | 285.9278 | 4 | 59632.499 | 372226.7608 | 431859.2597 | 0 | 0 | NORMAL
0.016952 | 275.3722 | 0.022163 | 297.0389 | 1 | 20939.5542 | 86145.2186 | 107084.7728 | 0 | 0 | NORMAL
0.016952 | 275.3722 | 0.022163 | 297.0389 | 2 | 32193.6865 | 172290.4372 | 204484.1237 | 0 | 0 | NORMAL
0.016952 | 275.3722 | 0.022163 | 297.0389 | 3 | 48345.3996 | 258435.6558 | 306781.0554 | 0 | 0 | NORMAL
0.016952 | 275.3722 | 0.022163 | 297.0389 | 4 | 69394.6933 | 344580.8744 | 413975.5677 | 0 | 0 | NORMAL
0.016952 | 275.3722 | 0.022163 | 308.15 | 1 | 24141.7743 | 75912.2744 | 100054.0487 | 0 | 0 | NORMAL
0.016952 | 275.3722 | 0.022163 | 308.15 | 2 | 37116.9657 | 151824.5488 | 188941.5146 | 0 | 0 | NORMAL
0.016952 | 275.3722 | 0.022163 | 308.15 | 3 | 55738.7094 | 227736.8233 | 283475.5327 | 0 | 0 | NORMAL
0.016952 | 275.3722 | 0.022163 | 308.15 | 4 | 80007.0054 | 303649.0977 | 383656.1031 | 0 | 0 | NORMAL
0.016952 | 275.3722 | 0.022163 | 319.2611 | 1 | 26078.8199 | 62357.8576 | 88436.6775 | 0 | 0 | NORMAL
0.016952 | 275.3722 | 0.022163 | 319.2611 | 2 | 40095.0921 | 124715.7153 | 164810.8074 | 0 | 0 | NORMAL
0.016952 | 275.3722 | 0.022163 | 319.2611 | 3 | 60210.9748 | 187073.5729 | 247284.5477 | 0 | 0 | NORMAL
0.016952 | 275.3722 | 0.022163 | 319.2611 | 4 | 86426.468 | 249431.4306 | 335857.8986 | 0 | 0 | NORMAL
0.016952 | 281.6685 | 0.022163 | 285.9278 | 1 | 18761.6504 | 114879.2034 | 133640.8538 | 0 | 0 | NORMAL
0.016952 | 281.6685 | 0.022163 | 285.9278 | 2 | 28845.2509 | 229758.4068 | 258603.6576 | 0 | 0 | NORMAL
0.016952 | 281.6685 | 0.022163 | 285.9278 | 3 | 43317.0391 | 344637.6101 | 387954.6493 | 0 | 0 | NORMAL
0.016952 | 281.6685 | 0.022163 | 285.9278 | 4 | 62177.0152 | 459516.8135 | 521693.8287 | 0 | 0 | NORMAL
0.016952 | 281.6685 | 0.022163 | 297.0389 | 1 | 22306.9592 | 108244.5212 | 130551.4804 | 0 | 0 | NORMAL
0.016952 | 281.6685 | 0.022163 | 297.0389 | 2 | 34296.0145 | 216489.0423 | 250785.0568 | 0 | 0 | NORMAL
0.016952 | 281.6685 | 0.022163 | 297.0389 | 3 | 51502.4747 | 324733.5635 | 376236.0382 | 0 | 0 | NORMAL
0.016952 | 281.6685 | 0.022163 | 297.0389 | 4 | 73926.3397 | 432978.0847 | 506904.4244 | 0 | 0 | NORMAL
0.016952 | 281.6685 | 0.022163 | 308.15 | 1 | 26939.2001 | 98288.3664 | 125227.5664 | 0 | 0 | NORMAL
0.016952 | 281.6685 | 0.022163 | 308.15 | 2 | 41417.8905 | 196576.7327 | 237994.6233 | 0 | 0 | NORMAL
0.016952 | 281.6685 | 0.022163 | 308.15 | 3 | 62197.427 | 294865.0991 | 357062.5261 | 0 | 0 | NORMAL
0.016952 | 281.6685 | 0.022163 | 308.15 | 4 | 89277.8094 | 393153.4655 | 482431.2749 | 0 | 0 | NORMAL
0.016952 | 281.6685 | 0.022163 | 319.2611 | 1 | 31226.8442 | 85010.739 | 116237.5832 | 0 | 0 | NORMAL
0.016952 | 281.6685 | 0.022163 | 319.2611 | 2 | 48009.9637 | 170021.478 | 218031.4416 | 0 | 0 | NORMAL
0.016952 | 281.6685 | 0.022163 | 319.2611 | 3 | 72096.772 | 255032.2169 | 327128.9889 | 0 | 0 | NORMAL
0.016952 | 281.6685 | 0.022163 | 319.2611 | 4 | 103487.2692 | 340042.9559 | 443530.2251 | 0 | 0 | NORMAL
0.016952 | 287.9648 | 0.022163 | 285.9278 | 1 | 19398.8743 | 119683.7827 | 139082.657 | 0 | 0 | NORMAL
0.016952 | 287.9648 | 0.022163 | 285.9278 | 2 | 29824.9559 | 239367.5654 | 269192.5212 | 0 | 0 | NORMAL
0.016952 | 287.9648 | 0.022163 | 285.9278 | 3 | 44788.2664 | 359051.348 | 403839.6145 | 0 | 0 | NORMAL
0.016952 | 287.9648 | 0.022163 | 285.9278 | 4 | 64288.806 | 478735.1307 | 543023.9367 | 0 | 0 | NORMAL
0.016952 | 287.9648 | 0.022163 | 297.0389 | 1 | 22427.431 | 113325.8899 | 135753.3209 | 0 | 0 | NORMAL
0.016952 | 287.9648 | 0.022163 | 297.0389 | 2 | 34481.2349 | 226651.7797 | 261133.0146 | 0 | 0 | NORMAL
0.016952 | 287.9648 | 0.022163 | 297.0389 | 3 | 51780.6209 | 339977.6696 | 391758.2905 | 0 | 0 | NORMAL
0.016952 | 287.9648 | 0.022163 | 297.0389 | 4 | 74325.5891 | 453303.5594 | 527629.1486 | 0 | 0 | NORMAL
0.016952 | 287.9648 | 0.022163 | 308.15 | 1 | 26840.3818 | 103646.5244 | 130486.9062 | 0 | 0 | NORMAL
0.016952 | 287.9648 | 0.022163 | 308.15 | 2 | 41265.9616 | 207293.0489 | 248559.0104 | 0 | 0 | NORMAL
0.016952 | 287.9648 | 0.022163 | 308.15 | 3 | 61969.2746 | 310939.5733 | 372908.8479 | 0 | 0 | NORMAL
0.016952 | 287.9648 | 0.022163 | 308.15 | 4 | 88950.3208 | 414586.0977 | 503536.4186 | 0 | 0 | NORMAL
0.016952 | 287.9648 | 0.022163 | 319.2611 | 1 | 31296.363 | 90645.6864 | 121942.0495 | 0 | 0 | NORMAL
0.016952 | 287.9648 | 0.022163 | 319.2611 | 2 | 48116.8459 | 181291.3729 | 229408.2188 | 0 | 0 | NORMAL
0.016952 | 287.9648 | 0.022163 | 319.2611 | 3 | 72257.2775 | 271937.0593 | 344194.3368 | 0 | 0 | NORMAL
0.016952 | 287.9648 | 0.022163 | 319.2611 | 4 | 103717.6579 | 362582.7457 | 466300.4036 | 0 | 0 | NORMAL
0.016952 | 294.2611 | 0.022163 | 285.9278 | 1 | 20383.7685 | 107470.4281 | 127854.1966 | 0 | 0 | NORMAL
0.016952 | 294.2611 | 0.022163 | 285.9278 | 2 | 31339.1894 | 214940.8562 | 246280.0456 | 0 | 0 | NORMAL
0.016952 | 294.2611 | 0.022163 | 285.9278 | 3 | 47062.1976 | 322411.2843 | 369473.4819 | 0 | 0 | NORMAL
0.016952 | 294.2611 | 0.022163 | 285.9278 | 4 | 67552.7929 | 429881.7124 | 497434.5053 | 0 | 0 | NORMAL
0.016952 | 294.2611 | 0.022163 | 297.0389 | 1 | 22157.7255 | 101389.3247 | 123547.0502 | 0 | 0 | NORMAL
0.016952 | 294.2611 | 0.022163 | 297.0389 | 2 | 34066.5739 | 202778.6493 | 236845.2232 | 0 | 0 | NORMAL
0.016952 | 294.2611 | 0.022163 | 297.0389 | 3 | 51157.9227 | 304167.974 | 355325.8967 | 0 | 0 | NORMAL
0.016952 | 294.2611 | 0.022163 | 297.0389 | 4 | 73431.772 | 405557.2986 | 478989.0706 | 0 | 0 | NORMAL
0.016952 | 294.2611 | 0.022163 | 308.15 | 1 | 25080.5878 | 91986.7486 | 117067.3364 | 0 | 0 | NORMAL
0.016952 | 294.2611 | 0.022163 | 308.15 | 2 | 38560.3521 | 183973.4972 | 222533.8493 | 0 | 0 | NORMAL
0.016952 | 294.2611 | 0.022163 | 308.15 | 3 | 57906.249 | 275960.2459 | 333866.4949 | 0 | 0 | NORMAL
0.016952 | 294.2611 | 0.022163 | 308.15 | 4 | 83118.2786 | 367946.9945 | 451065.2731 | 0 | 0 | NORMAL
0.016952 | 294.2611 | 0.022163 | 319.2611 | 1 | 27901.1572 | 79262.7 | 107163.8572 | 0 | 0 | NORMAL
0.016952 | 294.2611 | 0.022163 | 319.2611 | 2 | 42896.8592 | 158525.4 | 201422.2592 | 0 | 0 | NORMAL
0.016952 | 294.2611 | 0.022163 | 319.2611 | 3 | 64418.4008 | 237788.1 | 302206.5007 | 0 | 0 | NORMAL
0.016952 | 294.2611 | 0.022163 | 319.2611 | 4 | 92465.7817 | 317050.8 | 409516.5817 | 0 | 0 | NORMAL
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on J3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).
Note on K3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation