## RS0001
RS0001: Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 3.0.0 |  | ✓
| description | ASHRAE 90.1-2022 Appendix J curve set 'E': 150.0-300.0 ton, 5.33 COP, 6.51 IPLV liquid-cooled, positive displacement compressor chiller |  | ✓
| id | 94ab07ae-4f09-4788-8dd7-62bb3a4b6e3e |  | ✓
| data_timestamp | 2025-02-18T13:40Z |  | ✓
| data_version | 3 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2022 Appendix J curve set 'E' for Energy Cost Budget (ECB) Path A
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | SCROLL
performance |  |  |  | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| cycling_degradation_coefficient | 0 | - | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
performance.performance_map_evaporator_liquid_pressure_differential |  | $performance_map_evaporator_liqu |  | ✓
| condenser_type | LIQUID |  | ✓
performance.condenser_liquid_type
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| condenser_fouling_factor | 0 | m2-K/W
performance.performance_map_condenser_liquid_pressure_differential |  | $performance_map_condenser_liqui
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
performance.scaling
| minimum | 0.66667 | -
| maximum | 1.3333 | -
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on B20: Type of compressor speed control
Note on B21: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A22: Type of liquid in evaporator
Note on A23: An array of all liquid components within the liquid mixture
Note on B24: Defines whether concentration is defined on a volume or mass basis
Note on B25: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on A26: Data group describing the liquid pressure differential through the evaporator
Note on B27: Heat rejection method of the condenser
Note on A28: Type of liquid in condenser
Note on A29: An array of all liquid components within the liquid mixture
Note on B30: Defines whether concentration is defined on a volume or mass basis
Note on B31: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on A32: Data group describing the liquid pressure differential through the condenser
Note on A33: Data group describing cooling performance over a range of conditions
Note on A34: Data group describing standby performance
Note on A35: Specifies the range the performance data can be scaled to represent different capacity equipment
Note on B36: Minimum scaling factor
Note on B37: Maximum scaling factor

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_evaporator_liqu
performance.performance_map_evaporator_liquid_pressure_differential
grid_variables |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | evaporator_liquid_differential_pressure
m3/s | K | Pa
0.033905 | 275.3722 | 15000
0.033905 | 281.6685 | 15000
0.033905 | 287.9648 | 15000
0.033905 | 294.2611 | 15000
Note on A2: Data group defining the grid variables for the evaporator liquid pressure differential
Note on C2: Data group defining the lookup variables for the evaporator liquid pressure differential
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Pressure difference across the evaporator

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_condenser_liqui
performance.performance_map_condenser_liquid_pressure_differential
grid_variables |  | lookup_variables
condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | condenser_liquid_differential_pressure
m3/s | K | Pa
0.043699 | 285.9278 | 15000
0.043699 | 297.0389 | 15000
0.043699 | 308.15 | 15000
0.043699 | 319.2611 | 15000
Note on A2: Data group defining the grid variables for the condenser liquid pressure differential
Note on C2: Data group defining the lookup variables for the condenser liquid pressure differential
Note on A3: Condenser liquid flow
Note on B3: Entering condenser liquid temperature
Note on C3: Pressure difference across the condenser

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | oil_cooler_heat | auxiliary_heat | operation_state
m3/s | K | m3/s | K | - | W | W | W | W | W | -
0.033905 | 275.3722 | 0.043699 | 285.9278 | 1 | 34458.8555 | 182428.4654 | 216887.3209 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043699 | 285.9278 | 2 | 50455.6133 | 364856.9309 | 415312.5441 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043699 | 285.9278 | 3 | 73886.9179 | 547285.3963 | 621172.3142 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043699 | 285.9278 | 4 | 104752.7693 | 729713.8617 | 834466.631 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043699 | 297.0389 | 1 | 43446.6898 | 179250.5977 | 222697.2875 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043699 | 297.0389 | 2 | 63615.8498 | 358501.1954 | 422117.0452 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043699 | 297.0389 | 3 | 93158.6947 | 537751.793 | 630910.4878 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043699 | 297.0389 | 4 | 132075.2244 | 717002.3907 | 849077.6151 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043699 | 308.15 | 1 | 50710.8275 | 164984.8729 | 215695.7004 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043699 | 308.15 | 2 | 74252.2021 | 329969.7458 | 404221.9479 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043699 | 308.15 | 3 | 108734.5094 | 494954.6187 | 603689.1281 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043699 | 308.15 | 4 | 154157.7496 | 659939.4916 | 814097.2412 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043699 | 319.2611 | 1 | 53597.5328 | 139631.2911 | 193228.8239 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043699 | 319.2611 | 2 | 78478.9961 | 279262.5821 | 357741.5782 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043699 | 319.2611 | 3 | 114924.203 | 418893.8732 | 533818.0762 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043699 | 319.2611 | 4 | 162933.1534 | 558525.1643 | 721458.3177 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043699 | 285.9278 | 1 | 34685.6995 | 209642.1207 | 244327.8203 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043699 | 285.9278 | 2 | 50787.7646 | 419284.2415 | 470072.0061 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043699 | 285.9278 | 3 | 74373.3184 | 628926.3622 | 703299.6807 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043699 | 285.9278 | 4 | 105442.361 | 838568.483 | 944010.844 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043699 | 297.0389 | 1 | 44238.9765 | 209052.2337 | 253291.2102 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043699 | 297.0389 | 2 | 64775.9381 | 418104.4675 | 482880.4055 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043699 | 297.0389 | 3 | 94857.5215 | 627156.7012 | 722014.2226 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043699 | 297.0389 | 4 | 134483.7266 | 836208.9349 | 970692.6615 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043699 | 308.15 | 1 | 53148.7557 | 197374.4897 | 250523.2454 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043699 | 308.15 | 2 | 77821.8843 | 394748.9793 | 472570.8636 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043699 | 308.15 | 3 | 113961.9321 | 592123.469 | 706085.4011 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043699 | 308.15 | 4 | 161568.8992 | 789497.9587 | 951066.8579 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043699 | 319.2611 | 1 | 59094.2198 | 174608.8886 | 233703.1084 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043699 | 319.2611 | 2 | 86527.3979 | 349217.7772 | 435745.175 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043699 | 319.2611 | 3 | 126710.2375 | 523826.6657 | 650536.9032 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043699 | 319.2611 | 4 | 179642.7387 | 698435.5543 | 878078.293 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043699 | 285.9278 | 1 | 35760.1171 | 213611.0037 | 249371.1208 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043699 | 285.9278 | 2 | 52360.9566 | 427222.0074 | 479582.9641 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043699 | 285.9278 | 3 | 76677.0921 | 640833.0111 | 717510.1032 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043699 | 285.9278 | 4 | 108708.5234 | 854444.0148 | 963152.5382 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043699 | 297.0389 | 1 | 44468.843 | 215609.0974 | 260077.9404 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043699 | 297.0389 | 2 | 65112.515 | 431218.1948 | 496330.7098 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043699 | 297.0389 | 3 | 95350.4028 | 646827.2922 | 742177.695 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043699 | 297.0389 | 4 | 135182.5064 | 862436.3897 | 997618.896 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043699 | 308.15 | 1 | 52989.6381 | 206519.3341 | 259508.9722 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043699 | 308.15 | 2 | 77588.8998 | 413038.6682 | 490627.568 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043699 | 308.15 | 3 | 113620.7509 | 619558.0023 | 733178.7532 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043699 | 308.15 | 4 | 161085.1915 | 826077.3363 | 987162.5278 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043699 | 319.2611 | 1 | 59334.6035 | 186341.7137 | 245676.3173 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043699 | 319.2611 | 2 | 86879.3745 | 372683.4274 | 459562.8019 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043699 | 319.2611 | 3 | 127225.67 | 559025.1412 | 686250.8112 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043699 | 319.2611 | 4 | 180373.4903 | 745366.8549 | 925740.3452 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043699 | 285.9278 | 1 | 37848.0797 | 194335.1143 | 232183.194 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043699 | 285.9278 | 2 | 55418.2095 | 388670.2286 | 444088.4381 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043699 | 285.9278 | 3 | 81154.116 | 583005.3429 | 664159.4589 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043699 | 285.9278 | 4 | 115055.7993 | 777340.4572 | 892396.2565 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043699 | 297.0389 | 1 | 45010.2194 | 198921.1887 | 243931.4081 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043699 | 297.0389 | 2 | 65905.2133 | 397842.3775 | 463747.5908 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043699 | 297.0389 | 3 | 96511.2258 | 596763.5662 | 693274.792 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043699 | 297.0389 | 4 | 136828.2568 | 795684.755 | 932513.0118 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043699 | 308.15 | 1 | 51815.3635 | 192419.4061 | 244234.7697 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043699 | 308.15 | 2 | 75869.4944 | 384838.8123 | 460708.3067 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043699 | 308.15 | 3 | 111102.8632 | 577258.2184 | 688361.0817 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043699 | 308.15 | 4 | 157515.4701 | 769677.6246 | 927193.0947 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043699 | 319.2611 | 1 | 56608.5317 | 174829.7665 | 231438.2982 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043699 | 319.2611 | 2 | 82887.7844 | 349659.533 | 432547.3174 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043699 | 319.2611 | 3 | 121380.4079 | 524489.2995 | 645869.7074 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043699 | 319.2611 | 4 | 172086.4022 | 699319.066 | 871405.4682 | 0 | 0 | NORMAL
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on J3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).
Note on K3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation