## RS0001
RS0001: Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 3.0.0 |  | ✓
| description | ASHRAE 90.1-2022 Appendix J curve set 'F': 300.0-600.0 ton, 5.77 COP, 6.76 IPLV liquid-cooled, positive displacement compressor chiller |  | ✓
| id | 637da270-d079-4811-813e-c08c5a1b437b |  | ✓
| data_timestamp | 2025-02-18T13:40Z |  | ✓
| data_version | 3 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2022 Appendix J curve set 'F' for Energy Cost Budget (ECB) Path A
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | SCROLL
performance |  |  |  | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| cycling_degradation_coefficient | 0 | - | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
performance.performance_map_evaporator_liquid_pressure_differential |  | $performance_map_evaporator_liqu |  | ✓
| condenser_type | LIQUID |  | ✓
performance.condenser_liquid_type
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| condenser_fouling_factor | 0 | m2-K/W
performance.performance_map_condenser_liquid_pressure_differential |  | $performance_map_condenser_liqui
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
performance.scaling
| minimum | 0.66667 | -
| maximum | 1.3333 | -
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on B20: Type of compressor speed control
Note on B21: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A22: Type of liquid in evaporator
Note on A23: An array of all liquid components within the liquid mixture
Note on B24: Defines whether concentration is defined on a volume or mass basis
Note on B25: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on A26: Data group describing the liquid pressure differential through the evaporator
Note on B27: Heat rejection method of the condenser
Note on A28: Type of liquid in condenser
Note on A29: An array of all liquid components within the liquid mixture
Note on B30: Defines whether concentration is defined on a volume or mass basis
Note on B31: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on A32: Data group describing the liquid pressure differential through the condenser
Note on A33: Data group describing cooling performance over a range of conditions
Note on A34: Data group describing standby performance
Note on A35: Specifies the range the performance data can be scaled to represent different capacity equipment
Note on B36: Minimum scaling factor
Note on B37: Maximum scaling factor

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_evaporator_liqu
performance.performance_map_evaporator_liquid_pressure_differential
grid_variables |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | evaporator_liquid_differential_pressure
m3/s | K | Pa
0.067809 | 275.3722 | 15000
0.067809 | 281.6685 | 15000
0.067809 | 287.9648 | 15000
0.067809 | 294.2611 | 15000
Note on A2: Data group defining the grid variables for the evaporator liquid pressure differential
Note on C2: Data group defining the lookup variables for the evaporator liquid pressure differential
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Pressure difference across the evaporator

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_condenser_liqui
performance.performance_map_condenser_liquid_pressure_differential
grid_variables |  | lookup_variables
condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | condenser_liquid_differential_pressure
m3/s | K | Pa
0.086352 | 285.9278 | 15000
0.086352 | 297.0389 | 15000
0.086352 | 308.15 | 15000
0.086352 | 319.2611 | 15000
Note on A2: Data group defining the grid variables for the condenser liquid pressure differential
Note on C2: Data group defining the lookup variables for the condenser liquid pressure differential
Note on A3: Condenser liquid flow
Note on B3: Entering condenser liquid temperature
Note on C3: Pressure difference across the condenser

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | oil_cooler_heat | auxiliary_heat | operation_state
m3/s | K | m3/s | K | - | W | W | W | W | W | -
0.067809 | 275.3722 | 0.086352 | 285.9278 | 1 | 70389.5322 | 375690.6659 | 446080.1982 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.086352 | 285.9278 | 2 | 103084.4506 | 751381.3319 | 854465.7825 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.086352 | 285.9278 | 3 | 149863.5437 | 1127071.9978 | 1276935.5414 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.086352 | 285.9278 | 4 | 210726.8113 | 1502762.6637 | 1713489.475 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.086352 | 297.0389 | 1 | 86381.722 | 368337.0233 | 454718.7453 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.086352 | 297.0389 | 2 | 126504.781 | 736674.0466 | 863178.8276 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.086352 | 297.0389 | 3 | 183911.8766 | 1105011.0699 | 1288922.9465 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.086352 | 297.0389 | 4 | 258603.0089 | 1473348.0932 | 1731951.1022 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.086352 | 308.15 | 1 | 96415.4324 | 341738.3777 | 438153.8101 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.086352 | 308.15 | 2 | 141199.0045 | 683476.7554 | 824675.7599 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.086352 | 308.15 | 3 | 205274.2489 | 1025215.1331 | 1230489.3821 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.086352 | 308.15 | 4 | 288641.1656 | 1366953.5108 | 1655594.6764 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.086352 | 319.2611 | 1 | 97705.2493 | 295894.7292 | 393599.9784 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.086352 | 319.2611 | 2 | 143087.9227 | 591789.4583 | 734877.381 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.086352 | 319.2611 | 3 | 208020.3466 | 887684.1875 | 1095704.5341 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.086352 | 319.2611 | 4 | 292502.521 | 1183578.9166 | 1476081.4377 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.086352 | 285.9278 | 1 | 66361.9536 | 413527.3132 | 479889.2669 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.086352 | 285.9278 | 2 | 97186.1201 | 827054.6265 | 924240.7466 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.086352 | 285.9278 | 3 | 141288.5869 | 1240581.9397 | 1381870.5266 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.086352 | 285.9278 | 4 | 198669.3538 | 1654109.2529 | 1852778.6068 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.086352 | 297.0389 | 1 | 83657.2421 | 413591.6261 | 497248.8682 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.086352 | 297.0389 | 2 | 122514.8196 | 827183.2521 | 949698.0717 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.086352 | 297.0389 | 3 | 178111.2952 | 1240774.8782 | 1418886.1734 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.086352 | 297.0389 | 4 | 250446.6689 | 1654366.5042 | 1904813.1731 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.086352 | 308.15 | 1 | 96440.8967 | 394410.9359 | 490851.8327 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.086352 | 308.15 | 2 | 141236.2967 | 788821.8718 | 930058.1686 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.086352 | 308.15 | 3 | 205328.4641 | 1183232.8078 | 1388561.2719 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.086352 | 308.15 | 4 | 288717.3989 | 1577643.7437 | 1866361.1426 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.086352 | 319.2611 | 1 | 102247.4334 | 355985.2428 | 458232.6762 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.086352 | 319.2611 | 2 | 149739.8855 | 711970.4857 | 861710.3712 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.086352 | 319.2611 | 3 | 217690.9295 | 1067955.7285 | 1285646.658 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.086352 | 319.2611 | 4 | 306100.5652 | 1423940.9713 | 1730041.5365 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.086352 | 285.9278 | 1 | 66181.6528 | 415759.6196 | 481941.2724 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.086352 | 285.9278 | 2 | 96922.0721 | 831519.2392 | 928441.3113 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.086352 | 285.9278 | 3 | 140904.7155 | 1247278.8588 | 1388183.5743 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.086352 | 285.9278 | 4 | 198129.5828 | 1663038.4784 | 1861168.0613 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.086352 | 297.0389 | 1 | 82790.0841 | 423241.8879 | 506031.972 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.086352 | 297.0389 | 2 | 121244.8793 | 846483.7758 | 967728.655 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.086352 | 297.0389 | 3 | 176265.0637 | 1269725.6637 | 1445990.7273 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.086352 | 297.0389 | 4 | 247850.6374 | 1692967.5516 | 1940818.1889 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.086352 | 308.15 | 1 | 95665.8509 | 411479.1532 | 507145.0042 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.086352 | 308.15 | 2 | 140101.2534 | 822958.3064 | 963059.5598 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.086352 | 308.15 | 3 | 203678.345 | 1234437.4596 | 1438115.8046 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.086352 | 308.15 | 4 | 286397.1259 | 1645916.6128 | 1932313.7387 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.086352 | 319.2611 | 1 | 102663.399 | 380471.4156 | 483134.8146 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.086352 | 319.2611 | 2 | 150349.0612 | 760942.8311 | 911291.8923 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.086352 | 319.2611 | 3 | 218576.5453 | 1141414.2467 | 1359990.792 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.086352 | 319.2611 | 4 | 307345.8514 | 1521885.6623 | 1829231.5137 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.086352 | 285.9278 | 1 | 70158.3409 | 382387.585 | 452545.926 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.086352 | 285.9278 | 2 | 102745.8743 | 764775.1701 | 867521.0444 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.086352 | 285.9278 | 3 | 149371.3235 | 1147162.7551 | 1296534.0787 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.086352 | 285.9278 | 4 | 210034.6885 | 1529550.3402 | 1739585.0287 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.086352 | 297.0389 | 1 | 85232.4758 | 397287.8088 | 482520.2846 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.086352 | 297.0389 | 2 | 124821.7265 | 794575.6176 | 919397.3441 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.086352 | 297.0389 | 3 | 181465.0624 | 1191863.4264 | 1373328.4887 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.086352 | 297.0389 | 4 | 255162.4833 | 1589151.2351 | 1844313.7185 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.086352 | 308.15 | 1 | 96685.0393 | 392943.0296 | 489628.0689 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.086352 | 308.15 | 2 | 141593.8399 | 785886.0591 | 927479.8991 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.086352 | 308.15 | 3 | 205848.2582 | 1178829.0887 | 1384677.3469 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.086352 | 308.15 | 4 | 289448.2942 | 1571772.1183 | 1861220.4125 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.086352 | 319.2611 | 1 | 102690.407 | 369353.2474 | 472043.6544 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.086352 | 319.2611 | 2 | 150388.614 | 738706.4948 | 889095.1088 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.086352 | 319.2611 | 3 | 218634.047 | 1108059.7421 | 1326693.7891 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.086352 | 319.2611 | 4 | 307426.7059 | 1477412.9895 | 1784839.6954 | 0 | 0 | NORMAL
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on J3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).
Note on K3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation