## RS0001
RS0001: Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 3.0.0 |  | ✓
| description | ASHRAE 90.1-2022 Appendix J curve set 'G': 600.0+ ton, 6.28 COP, 7.03 IPLV liquid-cooled, positive displacement compressor chiller |  | ✓
| id | 073cbd1c-c2ea-4ce2-8fcf-0fb0f32b6518 |  | ✓
| data_timestamp | 2025-02-18T13:40Z |  | ✓
| data_version | 3 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2022 Appendix J curve set 'G' for Energy Cost Budget (ECB) Path A
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | SCROLL
performance |  |  |  | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| cycling_degradation_coefficient | 0 | - | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
performance.performance_map_evaporator_liquid_pressure_differential |  | $performance_map_evaporator_liqu |  | ✓
| condenser_type | LIQUID |  | ✓
performance.condenser_liquid_type
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| condenser_fouling_factor | 0 | m2-K/W
performance.performance_map_condenser_liquid_pressure_differential |  | $performance_map_condenser_liqui
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
performance.scaling
| minimum | 0.92308 | -
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on B20: Type of compressor speed control
Note on B21: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A22: Type of liquid in evaporator
Note on A23: An array of all liquid components within the liquid mixture
Note on B24: Defines whether concentration is defined on a volume or mass basis
Note on B25: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on A26: Data group describing the liquid pressure differential through the evaporator
Note on B27: Heat rejection method of the condenser
Note on A28: Type of liquid in condenser
Note on A29: An array of all liquid components within the liquid mixture
Note on B30: Defines whether concentration is defined on a volume or mass basis
Note on B31: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on A32: Data group describing the liquid pressure differential through the condenser
Note on A33: Data group describing cooling performance over a range of conditions
Note on A34: Data group describing standby performance
Note on A35: Specifies the range the performance data can be scaled to represent different capacity equipment
Note on B36: Minimum scaling factor

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_evaporator_liqu
performance.performance_map_evaporator_liquid_pressure_differential
grid_variables |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | evaporator_liquid_differential_pressure
m3/s | K | Pa
0.097947 | 275.3722 | 15000
0.097947 | 281.6685 | 15000
0.097947 | 287.9648 | 15000
0.097947 | 294.2611 | 15000
Note on A2: Data group defining the grid variables for the evaporator liquid pressure differential
Note on C2: Data group defining the lookup variables for the evaporator liquid pressure differential
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Pressure difference across the evaporator

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_condenser_liqui
performance.performance_map_condenser_liquid_pressure_differential
grid_variables |  | lookup_variables
condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | condenser_liquid_differential_pressure
m3/s | K | Pa
0.12322 | 285.9278 | 15000
0.12322 | 297.0389 | 15000
0.12322 | 308.15 | 15000
0.12322 | 319.2611 | 15000
Note on A2: Data group defining the grid variables for the condenser liquid pressure differential
Note on C2: Data group defining the lookup variables for the condenser liquid pressure differential
Note on A3: Condenser liquid flow
Note on B3: Entering condenser liquid temperature
Note on C3: Pressure difference across the condenser

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | oil_cooler_heat | auxiliary_heat | operation_state
m3/s | K | m3/s | K | - | W | W | W | W | W | -
0.097947 | 275.3722 | 0.12322 | 285.9278 | 1 | 98664.6918 | 537989.5109 | 636654.2027 | 0 | 0 | NORMAL
0.097947 | 275.3722 | 0.12322 | 285.9278 | 2 | 140982.4873 | 1075979.0218 | 1216961.5091 | 0 | 0 | NORMAL
0.097947 | 275.3722 | 0.12322 | 285.9278 | 3 | 199474.2154 | 1613968.5327 | 1813442.748 | 0 | 0 | NORMAL
0.097947 | 275.3722 | 0.12322 | 285.9278 | 4 | 274139.876 | 2151958.0435 | 2426097.9195 | 0 | 0 | NORMAL
0.097947 | 275.3722 | 0.12322 | 297.0389 | 1 | 126313.5428 | 537363.6955 | 663677.2383 | 0 | 0 | NORMAL
0.097947 | 275.3722 | 0.12322 | 297.0389 | 2 | 180490.0732 | 1074727.391 | 1255217.4642 | 0 | 0 | NORMAL
0.097947 | 275.3722 | 0.12322 | 297.0389 | 3 | 255372.9645 | 1612091.0866 | 1867464.051 | 0 | 0 | NORMAL
0.097947 | 275.3722 | 0.12322 | 297.0389 | 4 | 350962.2167 | 2149454.7821 | 2500416.9988 | 0 | 0 | NORMAL
0.097947 | 275.3722 | 0.12322 | 308.15 | 1 | 137971.9066 | 499626.3939 | 637598.3005 | 0 | 0 | NORMAL
0.097947 | 275.3722 | 0.12322 | 308.15 | 2 | 197148.7693 | 999252.7878 | 1196401.5571 | 0 | 0 | NORMAL
0.097947 | 275.3722 | 0.12322 | 308.15 | 3 | 278943.1284 | 1498879.1817 | 1777822.3101 | 0 | 0 | NORMAL
0.097947 | 275.3722 | 0.12322 | 308.15 | 4 | 383354.9839 | 1998505.5756 | 2381860.5594 | 0 | 0 | NORMAL
0.097947 | 275.3722 | 0.12322 | 319.2611 | 1 | 130262.7321 | 424777.606 | 555040.3381 | 0 | 0 | NORMAL
0.097947 | 275.3722 | 0.12322 | 319.2611 | 2 | 186133.0901 | 849555.212 | 1035688.3022 | 0 | 0 | NORMAL
0.097947 | 275.3722 | 0.12322 | 319.2611 | 3 | 263357.1929 | 1274332.8181 | 1537690.0109 | 0 | 0 | NORMAL
0.097947 | 275.3722 | 0.12322 | 319.2611 | 4 | 361935.0404 | 1699110.4241 | 2061045.4644 | 0 | 0 | NORMAL
0.097947 | 281.6685 | 0.12322 | 285.9278 | 1 | 89624.9115 | 577333.8402 | 666958.7517 | 0 | 0 | NORMAL
0.097947 | 281.6685 | 0.12322 | 285.9278 | 2 | 128065.4986 | 1154667.6804 | 1282733.179 | 0 | 0 | NORMAL
0.097947 | 281.6685 | 0.12322 | 285.9278 | 3 | 181198.1426 | 1732001.5206 | 1913199.6633 | 0 | 0 | NORMAL
0.097947 | 281.6685 | 0.12322 | 285.9278 | 4 | 249022.8437 | 2309335.3608 | 2558358.2045 | 0 | 0 | NORMAL
0.097947 | 281.6685 | 0.12322 | 297.0389 | 1 | 119464.6891 | 591780.7444 | 711245.4336 | 0 | 0 | NORMAL
0.097947 | 281.6685 | 0.12322 | 297.0389 | 2 | 170703.7108 | 1183561.4889 | 1354265.1997 | 0 | 0 | NORMAL
0.097947 | 281.6685 | 0.12322 | 297.0389 | 3 | 241526.3727 | 1775342.2333 | 2016868.606 | 0 | 0 | NORMAL
0.097947 | 281.6685 | 0.12322 | 297.0389 | 4 | 331932.6747 | 2367122.9778 | 2699055.6525 | 0 | 0 | NORMAL
0.097947 | 281.6685 | 0.12322 | 308.15 | 1 | 135409.4622 | 569116.1624 | 704525.6246 | 0 | 0 | NORMAL
0.097947 | 281.6685 | 0.12322 | 308.15 | 2 | 193487.2793 | 1138232.3249 | 1331719.6041 | 0 | 0 | NORMAL
0.097947 | 281.6685 | 0.12322 | 308.15 | 3 | 273762.5357 | 1707348.4873 | 1981111.023 | 0 | 0 | NORMAL
0.097947 | 281.6685 | 0.12322 | 308.15 | 4 | 376235.2314 | 2276464.6497 | 2652699.8811 | 0 | 0 | NORMAL
0.097947 | 281.6685 | 0.12322 | 319.2611 | 1 | 134164.1578 | 509340.0942 | 643504.252 | 0 | 0 | NORMAL
0.097947 | 281.6685 | 0.12322 | 319.2611 | 2 | 191707.8574 | 1018680.1883 | 1210388.0457 | 0 | 0 | NORMAL
0.097947 | 281.6685 | 0.12322 | 319.2611 | 3 | 271244.8558 | 1528020.2825 | 1799265.1382 | 0 | 0 | NORMAL
0.097947 | 281.6685 | 0.12322 | 319.2611 | 4 | 372775.1528 | 2037360.3767 | 2410135.5294 | 0 | 0 | NORMAL
0.097947 | 287.9648 | 0.12322 | 285.9278 | 1 | 87441.06 | 573677.6062 | 661118.6663 | 0 | 0 | NORMAL
0.097947 | 287.9648 | 0.12322 | 285.9278 | 2 | 124944.9819 | 1147355.2125 | 1272300.1944 | 0 | 0 | NORMAL
0.097947 | 287.9648 | 0.12322 | 285.9278 | 3 | 176782.9658 | 1721032.8187 | 1897815.7845 | 0 | 0 | NORMAL
0.097947 | 287.9648 | 0.12322 | 285.9278 | 4 | 242955.0116 | 2294710.4249 | 2537665.4365 | 0 | 0 | NORMAL
0.097947 | 287.9648 | 0.12322 | 297.0389 | 1 | 117034.3883 | 603197.2301 | 720231.6184 | 0 | 0 | NORMAL
0.097947 | 287.9648 | 0.12322 | 297.0389 | 2 | 167231.0415 | 1206394.4602 | 1373625.5016 | 0 | 0 | NORMAL
0.097947 | 287.9648 | 0.12322 | 297.0389 | 3 | 236612.9397 | 1809591.6902 | 2046204.63 | 0 | 0 | NORMAL
0.097947 | 287.9648 | 0.12322 | 297.0389 | 4 | 325180.0832 | 2412788.9203 | 2737969.0035 | 0 | 0 | NORMAL
0.097947 | 287.9648 | 0.12322 | 308.15 | 1 | 134039.2836 | 595605.3677 | 729644.6513 | 0 | 0 | NORMAL
0.097947 | 287.9648 | 0.12322 | 308.15 | 2 | 191529.424 | 1191210.7353 | 1382740.1594 | 0 | 0 | NORMAL
0.097947 | 287.9648 | 0.12322 | 308.15 | 3 | 270992.3927 | 1786816.103 | 2057808.4958 | 0 | 0 | NORMAL
0.097947 | 287.9648 | 0.12322 | 308.15 | 4 | 372428.1898 | 2382421.4707 | 2754849.6604 | 0 | 0 | NORMAL
0.097947 | 287.9648 | 0.12322 | 319.2611 | 1 | 135242.651 | 550902.019 | 686144.67 | 0 | 0 | NORMAL
0.097947 | 287.9648 | 0.12322 | 319.2611 | 2 | 193248.922 | 1101804.038 | 1295052.96 | 0 | 0 | NORMAL
0.097947 | 287.9648 | 0.12322 | 319.2611 | 3 | 273425.2871 | 1652706.057 | 1926131.3442 | 0 | 0 | NORMAL
0.097947 | 287.9648 | 0.12322 | 319.2611 | 4 | 375771.7466 | 2203608.076 | 2579379.8226 | 0 | 0 | NORMAL
0.097947 | 294.2611 | 0.12322 | 285.9278 | 1 | 92198.6518 | 527020.809 | 619219.4608 | 0 | 0 | NORMAL
0.097947 | 294.2611 | 0.12322 | 285.9278 | 2 | 131743.1293 | 1054041.6179 | 1185784.7473 | 0 | 0 | NORMAL
0.097947 | 294.2611 | 0.12322 | 285.9278 | 3 | 186401.5727 | 1581062.4269 | 1767463.9996 | 0 | 0 | NORMAL
0.097947 | 294.2611 | 0.12322 | 285.9278 | 4 | 256173.9818 | 2108083.2359 | 2364257.2176 | 0 | 0 | NORMAL
0.097947 | 294.2611 | 0.12322 | 297.0389 | 1 | 120903.1094 | 571613.1524 | 692516.2618 | 0 | 0 | NORMAL
0.097947 | 294.2611 | 0.12322 | 297.0389 | 2 | 172759.077 | 1143226.3048 | 1315985.3818 | 0 | 0 | NORMAL
0.097947 | 294.2611 | 0.12322 | 297.0389 | 3 | 244434.4825 | 1714839.4573 | 1959273.9397 | 0 | 0 | NORMAL
0.097947 | 294.2611 | 0.12322 | 297.0389 | 4 | 335929.3259 | 2286452.6097 | 2622381.9356 | 0 | 0 | NORMAL
0.097947 | 294.2611 | 0.12322 | 308.15 | 1 | 137536.7943 | 579094.0096 | 716630.8039 | 0 | 0 | NORMAL
0.097947 | 294.2611 | 0.12322 | 308.15 | 2 | 196527.0351 | 1158188.0192 | 1354715.0544 | 0 | 0 | NORMAL
0.097947 | 294.2611 | 0.12322 | 308.15 | 3 | 278063.4451 | 1737282.0289 | 2015345.474 | 0 | 0 | NORMAL
0.097947 | 294.2611 | 0.12322 | 308.15 | 4 | 382146.0243 | 2316376.0385 | 2698522.0628 | 0 | 0 | NORMAL
0.097947 | 294.2611 | 0.12322 | 319.2611 | 1 | 138968.5898 | 549463.3806 | 688431.9704 | 0 | 0 | NORMAL
0.097947 | 294.2611 | 0.12322 | 319.2611 | 2 | 198572.9351 | 1098926.7611 | 1297499.6962 | 0 | 0 | NORMAL
0.097947 | 294.2611 | 0.12322 | 319.2611 | 3 | 280958.1614 | 1648390.1417 | 1929348.3031 | 0 | 0 | NORMAL
0.097947 | 294.2611 | 0.12322 | 319.2611 | 4 | 386124.2686 | 2197853.5223 | 2583977.7908 | 0 | 0 | NORMAL
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on J3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).
Note on K3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation