## RS0001
RS0001: Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 3.0.0 |  | ✓
| description | ASHRAE 90.1-2022 Appendix J curve set 'H': 0.0-300.0 ton, 5.77 COP, 6.39 IPLV liquid-cooled, centrifugal compressor chiller |  | ✓
| id | d81790ca-c9e2-44a2-bfa1-05e5e918e21c |  | ✓
| data_timestamp | 2025-02-18T13:40Z |  | ✓
| data_version | 3 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2022 Appendix J curve set 'H' for Energy Cost Budget (ECB) Path A
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | CENTRIFUGAL
performance |  |  |  | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| cycling_degradation_coefficient | 0 | - | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
performance.performance_map_evaporator_liquid_pressure_differential |  | $performance_map_evaporator_liqu |  | ✓
| condenser_type | LIQUID |  | ✓
performance.condenser_liquid_type
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| condenser_fouling_factor | 0 | m2-K/W
performance.performance_map_condenser_liquid_pressure_differential |  | $performance_map_condenser_liqui
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
performance.scaling
| maximum | 2 | -
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on B20: Type of compressor speed control
Note on B21: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A22: Type of liquid in evaporator
Note on A23: An array of all liquid components within the liquid mixture
Note on B24: Defines whether concentration is defined on a volume or mass basis
Note on B25: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on A26: Data group describing the liquid pressure differential through the evaporator
Note on B27: Heat rejection method of the condenser
Note on A28: Type of liquid in condenser
Note on A29: An array of all liquid components within the liquid mixture
Note on B30: Defines whether concentration is defined on a volume or mass basis
Note on B31: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on A32: Data group describing the liquid pressure differential through the condenser
Note on A33: Data group describing cooling performance over a range of conditions
Note on A34: Data group describing standby performance
Note on A35: Specifies the range the performance data can be scaled to represent different capacity equipment
Note on B36: Maximum scaling factor

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_evaporator_liqu
performance.performance_map_evaporator_liquid_pressure_differential
grid_variables |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | evaporator_liquid_differential_pressure
m3/s | K | Pa
0.022603 | 275.3722 | 15000
0.022603 | 281.6685 | 15000
0.022603 | 287.9648 | 15000
0.022603 | 294.2611 | 15000
Note on A2: Data group defining the grid variables for the evaporator liquid pressure differential
Note on C2: Data group defining the lookup variables for the evaporator liquid pressure differential
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Pressure difference across the evaporator

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_condenser_liqui
performance.performance_map_condenser_liquid_pressure_differential
grid_variables |  | lookup_variables
condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | condenser_liquid_differential_pressure
m3/s | K | Pa
0.028784 | 285.9278 | 15000
0.028784 | 297.0389 | 15000
0.028784 | 308.15 | 15000
0.028784 | 319.2611 | 15000
Note on A2: Data group defining the grid variables for the condenser liquid pressure differential
Note on C2: Data group defining the lookup variables for the condenser liquid pressure differential
Note on A3: Condenser liquid flow
Note on B3: Entering condenser liquid temperature
Note on C3: Pressure difference across the condenser

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | oil_cooler_heat | auxiliary_heat | operation_state
m3/s | K | m3/s | K | - | W | W | W | W | W | -
0.022603 | 275.3722 | 0.028784 | 285.9278 | 1 | 24921.2749 | 123457.9721 | 148379.247 | 0 | 0 | NORMAL
0.022603 | 275.3722 | 0.028784 | 285.9278 | 2 | 34226.915 | 246915.9442 | 281142.8593 | 0 | 0 | NORMAL
0.022603 | 275.3722 | 0.028784 | 285.9278 | 3 | 48887.6449 | 370373.9164 | 419261.5613 | 0 | 0 | NORMAL
0.022603 | 275.3722 | 0.028784 | 285.9278 | 4 | 68903.4647 | 493831.8885 | 562735.3532 | 0 | 0 | NORMAL
0.022603 | 275.3722 | 0.028784 | 297.0389 | 1 | 29536.0257 | 114914.1351 | 144450.1608 | 0 | 0 | NORMAL
0.022603 | 275.3722 | 0.028784 | 297.0389 | 2 | 40564.8204 | 229828.2703 | 270393.0907 | 0 | 0 | NORMAL
0.022603 | 275.3722 | 0.028784 | 297.0389 | 3 | 57940.3238 | 344742.4054 | 402682.7292 | 0 | 0 | NORMAL
0.022603 | 275.3722 | 0.028784 | 297.0389 | 4 | 81662.5357 | 459656.5406 | 541319.0763 | 0 | 0 | NORMAL
0.022603 | 275.3722 | 0.028784 | 308.15 | 1 | 26508.2811 | 95884.8651 | 122393.1462 | 0 | 0 | NORMAL
0.022603 | 275.3722 | 0.028784 | 308.15 | 2 | 36406.5117 | 191769.7302 | 228176.2418 | 0 | 0 | NORMAL
0.022603 | 275.3722 | 0.028784 | 308.15 | 3 | 52000.8483 | 287654.5953 | 339655.4436 | 0 | 0 | NORMAL
0.022603 | 275.3722 | 0.028784 | 308.15 | 4 | 73291.2911 | 383539.4603 | 456830.7514 | 0 | 0 | NORMAL
0.022603 | 275.3722 | 0.028784 | 319.2611 | 1 | 17266.7369 | 66370.1619 | 83636.8988 | 0 | 0 | NORMAL
0.022603 | 275.3722 | 0.028784 | 319.2611 | 2 | 23714.1615 | 132740.3239 | 156454.4853 | 0 | 0 | NORMAL
0.022603 | 275.3722 | 0.028784 | 319.2611 | 3 | 33871.8668 | 199110.4858 | 232982.3526 | 0 | 0 | NORMAL
0.022603 | 275.3722 | 0.028784 | 319.2611 | 4 | 47739.8528 | 265480.6478 | 313220.5006 | 0 | 0 | NORMAL
0.022603 | 281.6685 | 0.028784 | 285.9278 | 1 | 24152.2792 | 144675.293 | 168827.5722 | 0 | 0 | NORMAL
0.022603 | 281.6685 | 0.028784 | 285.9278 | 2 | 33170.7752 | 289350.586 | 322521.3613 | 0 | 0 | NORMAL
0.022603 | 281.6685 | 0.028784 | 285.9278 | 3 | 47379.1191 | 434025.879 | 481404.9981 | 0 | 0 | NORMAL
0.022603 | 281.6685 | 0.028784 | 285.9278 | 4 | 66777.3107 | 578701.172 | 645478.4828 | 0 | 0 | NORMAL
0.022603 | 281.6685 | 0.028784 | 297.0389 | 1 | 32655.8946 | 143567.8641 | 176223.7588 | 0 | 0 | NORMAL
0.022603 | 281.6685 | 0.028784 | 297.0389 | 2 | 44849.653 | 287135.7282 | 331985.3812 | 0 | 0 | NORMAL
0.022603 | 281.6685 | 0.028784 | 297.0389 | 3 | 64060.5181 | 430703.5923 | 494764.1105 | 0 | 0 | NORMAL
0.022603 | 281.6685 | 0.028784 | 297.0389 | 4 | 90288.4901 | 574271.4565 | 664559.9466 | 0 | 0 | NORMAL
0.022603 | 281.6685 | 0.028784 | 308.15 | 1 | 33289.9092 | 131975.0021 | 165264.9113 | 0 | 0 | NORMAL
0.022603 | 281.6685 | 0.028784 | 308.15 | 2 | 45720.4094 | 263950.0043 | 309670.4137 | 0 | 0 | NORMAL
0.022603 | 281.6685 | 0.028784 | 308.15 | 3 | 65304.2538 | 395925.0064 | 461229.2602 | 0 | 0 | NORMAL
0.022603 | 281.6685 | 0.028784 | 308.15 | 4 | 92041.4421 | 527900.0085 | 619941.4506 | 0 | 0 | NORMAL
0.022603 | 281.6685 | 0.028784 | 319.2611 | 1 | 26517.473 | 109896.7071 | 136414.1801 | 0 | 0 | NORMAL
0.022603 | 281.6685 | 0.028784 | 319.2611 | 2 | 36419.1358 | 219793.4141 | 256212.5499 | 0 | 0 | NORMAL
0.022603 | 281.6685 | 0.028784 | 319.2611 | 3 | 52018.8798 | 329690.1212 | 381709.001 | 0 | 0 | NORMAL
0.022603 | 281.6685 | 0.028784 | 319.2611 | 4 | 73316.7051 | 439586.8283 | 512903.5334 | 0 | 0 | NORMAL
0.022603 | 287.9648 | 0.028784 | 285.9278 | 1 | 20972.2453 | 143233.4049 | 164205.6501 | 0 | 0 | NORMAL
0.022603 | 287.9648 | 0.028784 | 285.9278 | 2 | 28803.312 | 286466.8097 | 315270.1217 | 0 | 0 | NORMAL
0.022603 | 287.9648 | 0.028784 | 285.9278 | 3 | 41140.9001 | 429700.2146 | 470841.1146 | 0 | 0 | NORMAL
0.022603 | 287.9648 | 0.028784 | 285.9278 | 4 | 57985.0095 | 572933.6194 | 630918.6289 | 0 | 0 | NORMAL
0.022603 | 287.9648 | 0.028784 | 297.0389 | 1 | 31750.6375 | 149562.384 | 181313.0215 | 0 | 0 | NORMAL
0.022603 | 287.9648 | 0.028784 | 297.0389 | 2 | 43606.3715 | 299124.7681 | 342731.1395 | 0 | 0 | NORMAL
0.022603 | 287.9648 | 0.028784 | 297.0389 | 3 | 62284.6904 | 448687.1521 | 510971.8425 | 0 | 0 | NORMAL
0.022603 | 287.9648 | 0.028784 | 297.0389 | 4 | 87785.5943 | 598249.5362 | 686035.1304 | 0 | 0 | NORMAL
0.022603 | 287.9648 | 0.028784 | 308.15 | 1 | 35250.2516 | 145405.9301 | 180656.1817 | 0 | 0 | NORMAL
0.022603 | 287.9648 | 0.028784 | 308.15 | 2 | 48412.7466 | 290811.8603 | 339224.6069 | 0 | 0 | NORMAL
0.022603 | 287.9648 | 0.028784 | 308.15 | 3 | 69149.8244 | 436217.7904 | 505367.6149 | 0 | 0 | NORMAL
0.022603 | 287.9648 | 0.028784 | 308.15 | 4 | 97461.4852 | 581623.7206 | 679085.2058 | 0 | 0 | NORMAL
0.022603 | 287.9648 | 0.028784 | 319.2611 | 1 | 30968.6924 | 130764.0432 | 161732.7356 | 0 | 0 | NORMAL
0.022603 | 287.9648 | 0.028784 | 319.2611 | 2 | 42532.447 | 261528.0863 | 304060.5333 | 0 | 0 | NORMAL
0.022603 | 287.9648 | 0.028784 | 319.2611 | 3 | 60750.7619 | 392292.1295 | 453042.8914 | 0 | 0 | NORMAL
0.022603 | 287.9648 | 0.028784 | 319.2611 | 4 | 85623.6373 | 523056.1726 | 608679.8099 | 0 | 0 | NORMAL
0.022603 | 294.2611 | 0.028784 | 285.9278 | 1 | 16713.876 | 119132.3076 | 135846.1837 | 0 | 0 | NORMAL
0.022603 | 294.2611 | 0.028784 | 285.9278 | 2 | 22954.8615 | 238264.6153 | 261219.4768 | 0 | 0 | NORMAL
0.022603 | 294.2611 | 0.028784 | 285.9278 | 3 | 32787.3289 | 357396.9229 | 390184.2518 | 0 | 0 | NORMAL
0.022603 | 294.2611 | 0.028784 | 285.9278 | 4 | 46211.2781 | 476529.2306 | 522740.5087 | 0 | 0 | NORMAL
0.022603 | 294.2611 | 0.028784 | 297.0389 | 1 | 28110.358 | 132897.6949 | 161008.0529 | 0 | 0 | NORMAL
0.022603 | 294.2611 | 0.028784 | 297.0389 | 2 | 38606.8063 | 265795.3898 | 304402.1962 | 0 | 0 | NORMAL
0.022603 | 294.2611 | 0.028784 | 297.0389 | 3 | 55143.6154 | 398693.0848 | 453836.7002 | 0 | 0 | NORMAL
0.022603 | 294.2611 | 0.028784 | 297.0389 | 4 | 77720.7853 | 531590.7797 | 609311.565 | 0 | 0 | NORMAL
0.022603 | 294.2611 | 0.028784 | 308.15 | 1 | 33636.8131 | 136177.6491 | 169814.4622 | 0 | 0 | NORMAL
0.022603 | 294.2611 | 0.028784 | 308.15 | 2 | 46196.8478 | 272355.2982 | 318552.1461 | 0 | 0 | NORMAL
0.022603 | 294.2611 | 0.028784 | 308.15 | 3 | 65984.7694 | 408532.9473 | 474517.7167 | 0 | 0 | NORMAL
0.022603 | 294.2611 | 0.028784 | 308.15 | 4 | 93000.5778 | 544710.5964 | 637711.1742 | 0 | 0 | NORMAL
0.022603 | 294.2611 | 0.028784 | 319.2611 | 1 | 31825.3008 | 128972.1702 | 160797.471 | 0 | 0 | NORMAL
0.022603 | 294.2611 | 0.028784 | 319.2611 | 2 | 43708.9141 | 257944.3404 | 301653.2546 | 0 | 0 | NORMAL
0.022603 | 294.2611 | 0.028784 | 319.2611 | 3 | 62431.1561 | 386916.5106 | 449347.6667 | 0 | 0 | NORMAL
0.022603 | 294.2611 | 0.028784 | 319.2611 | 4 | 87992.0267 | 515888.6808 | 603880.7075 | 0 | 0 | NORMAL
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on J3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).
Note on K3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation