## RS0001
RS0001: Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 3.0.0 |  | ✓
| description | ASHRAE 90.1-2022 Appendix J curve set 'I': 300.0-400.0 ton, 6.28 COP, 6.76 IPLV liquid-cooled, centrifugal compressor chiller |  | ✓
| id | 890bc9da-08a3-445e-b272-7ce88830ffaa |  | ✓
| data_timestamp | 2025-02-18T13:40Z |  | ✓
| data_version | 3 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2022 Appendix J curve set 'I' for Energy Cost Budget (ECB) Path A
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | CENTRIFUGAL
performance |  |  |  | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| cycling_degradation_coefficient | 0 | - | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
performance.performance_map_evaporator_liquid_pressure_differential |  | $performance_map_evaporator_liqu |  | ✓
| condenser_type | LIQUID |  | ✓
performance.condenser_liquid_type
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| condenser_fouling_factor | 0 | m2-K/W
performance.performance_map_condenser_liquid_pressure_differential |  | $performance_map_condenser_liqui
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
performance.scaling
| minimum | 0.85714 | -
| maximum | 1.1429 | -
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on B20: Type of compressor speed control
Note on B21: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A22: Type of liquid in evaporator
Note on A23: An array of all liquid components within the liquid mixture
Note on B24: Defines whether concentration is defined on a volume or mass basis
Note on B25: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on A26: Data group describing the liquid pressure differential through the evaporator
Note on B27: Heat rejection method of the condenser
Note on A28: Type of liquid in condenser
Note on A29: An array of all liquid components within the liquid mixture
Note on B30: Defines whether concentration is defined on a volume or mass basis
Note on B31: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on A32: Data group describing the liquid pressure differential through the condenser
Note on A33: Data group describing cooling performance over a range of conditions
Note on A34: Data group describing standby performance
Note on A35: Specifies the range the performance data can be scaled to represent different capacity equipment
Note on B36: Minimum scaling factor
Note on B37: Maximum scaling factor

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_evaporator_liqu
performance.performance_map_evaporator_liquid_pressure_differential
grid_variables |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | evaporator_liquid_differential_pressure
m3/s | K | Pa
0.052741 | 275.3722 | 15000
0.052741 | 281.6685 | 15000
0.052741 | 287.9648 | 15000
0.052741 | 294.2611 | 15000
Note on A2: Data group defining the grid variables for the evaporator liquid pressure differential
Note on C2: Data group defining the lookup variables for the evaporator liquid pressure differential
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Pressure difference across the evaporator

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_condenser_liqui
performance.performance_map_condenser_liquid_pressure_differential
grid_variables |  | lookup_variables
condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | condenser_liquid_differential_pressure
m3/s | K | Pa
0.066349 | 285.9278 | 15000
0.066349 | 297.0389 | 15000
0.066349 | 308.15 | 15000
0.066349 | 319.2611 | 15000
Note on A2: Data group defining the grid variables for the condenser liquid pressure differential
Note on C2: Data group defining the lookup variables for the condenser liquid pressure differential
Note on A3: Condenser liquid flow
Note on B3: Entering condenser liquid temperature
Note on C3: Pressure difference across the condenser

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | oil_cooler_heat | auxiliary_heat | operation_state
m3/s | K | m3/s | K | - | W | W | W | W | W | -
0.052741 | 275.3722 | 0.066349 | 285.9278 | 1 | 62660.2769 | 321808.1533 | 384468.4302 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.066349 | 285.9278 | 2 | 88725.6543 | 643616.3066 | 732341.961 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.066349 | 285.9278 | 3 | 129053.9541 | 965424.46 | 1094478.414 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.066349 | 285.9278 | 4 | 183645.1762 | 1287232.6133 | 1470877.7895 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.066349 | 297.0389 | 1 | 63742.4328 | 280419.5656 | 344161.9984 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.066349 | 297.0389 | 2 | 90257.9647 | 560839.1311 | 651097.0958 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.066349 | 297.0389 | 3 | 131282.7425 | 841258.6967 | 972541.4392 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.066349 | 297.0389 | 4 | 186816.7663 | 1121678.2623 | 1308495.0285 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.066349 | 308.15 | 1 | 60368.1868 | 254379.2204 | 314747.4072 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.066349 | 308.15 | 2 | 85480.1022 | 508758.4409 | 594238.5431 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.066349 | 308.15 | 3 | 124333.2074 | 763137.6613 | 887470.8688 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.066349 | 308.15 | 4 | 176927.5026 | 1017516.8817 | 1194444.3843 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.066349 | 319.2611 | 1 | 54763.1954 | 243687.1179 | 298450.3134 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.066349 | 319.2611 | 2 | 77543.5505 | 487374.2359 | 564917.7864 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.066349 | 319.2611 | 3 | 112789.2702 | 731061.3538 | 843850.6241 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.066349 | 319.2611 | 4 | 160500.3547 | 974748.4718 | 1135248.8265 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.066349 | 285.9278 | 1 | 61110.3748 | 361994.7322 | 423105.107 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.066349 | 285.9278 | 2 | 86531.025 | 723989.4645 | 810520.4894 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.066349 | 285.9278 | 3 | 125861.8041 | 1085984.1967 | 1211846.0008 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.066349 | 285.9278 | 4 | 179102.7122 | 1447978.9289 | 1627081.6411 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.066349 | 297.0389 | 1 | 67038.7855 | 330918.0867 | 397956.8722 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.066349 | 297.0389 | 2 | 94925.5318 | 661836.1734 | 756761.7052 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.066349 | 297.0389 | 3 | 138071.8499 | 992754.2601 | 1130826.11 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.066349 | 297.0389 | 4 | 196477.7398 | 1323672.3468 | 1520150.0866 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.066349 | 308.15 | 1 | 67374.8859 | 315189.6838 | 382564.5696 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.066349 | 308.15 | 2 | 95401.4429 | 630379.3676 | 725780.8105 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.066349 | 308.15 | 3 | 138764.076 | 945569.0514 | 1084333.1273 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.066349 | 308.15 | 4 | 197462.785 | 1260758.7352 | 1458221.5201 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.066349 | 319.2611 | 1 | 63699.3078 | 314809.5235 | 378508.8313 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.066349 | 319.2611 | 2 | 90196.9005 | 629619.0471 | 719815.9476 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.066349 | 319.2611 | 3 | 131193.923 | 944428.5706 | 1075622.4935 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.066349 | 319.2611 | 4 | 186690.3751 | 1259238.0941 | 1445928.4692 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.066349 | 285.9278 | 1 | 56222.7568 | 374171.8658 | 430394.6227 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.066349 | 285.9278 | 2 | 79610.2592 | 748343.7317 | 827953.9909 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.066349 | 285.9278 | 3 | 115795.3561 | 1122515.5975 | 1238310.9536 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.066349 | 285.9278 | 4 | 164778.0475 | 1496687.4634 | 1661465.5109 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.066349 | 297.0389 | 1 | 65450.4954 | 353407.1625 | 418857.6579 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.066349 | 297.0389 | 2 | 92676.5459 | 706814.3251 | 799490.871 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.066349 | 297.0389 | 3 | 134800.6368 | 1060221.4876 | 1195022.1244 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.066349 | 297.0389 | 4 | 191822.7681 | 1413628.6501 | 1605451.4182 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.066349 | 308.15 | 1 | 68743.797 | 347990.7019 | 416734.4989 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.066349 | 308.15 | 2 | 97339.7928 | 695981.4037 | 793321.1965 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.066349 | 308.15 | 3 | 141583.4602 | 1043972.1056 | 1185555.5657 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.066349 | 308.15 | 4 | 201474.7993 | 1391962.8074 | 1593437.6067 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.066349 | 319.2611 | 1 | 67038.2692 | 357922.4838 | 424960.753 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.066349 | 319.2611 | 2 | 94924.8008 | 715844.9676 | 810769.7684 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.066349 | 319.2611 | 3 | 138070.7865 | 1073767.4514 | 1211838.238 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.066349 | 319.2611 | 4 | 196476.2266 | 1431689.9353 | 1628166.1619 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.066349 | 285.9278 | 1 | 49824.8704 | 358339.5542 | 408164.4245 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.066349 | 285.9278 | 2 | 70550.9845 | 716679.1083 | 787230.0928 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.066349 | 285.9278 | 3 | 102618.3868 | 1075018.6625 | 1177637.0493 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.066349 | 285.9278 | 4 | 146027.0773 | 1433358.2166 | 1579385.2939 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.066349 | 297.0389 | 1 | 60933.7306 | 347886.7931 | 408820.5236 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.066349 | 297.0389 | 2 | 86280.9005 | 695773.5861 | 782054.4866 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.066349 | 297.0389 | 3 | 125497.991 | 1043660.3792 | 1169158.3702 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.066349 | 297.0389 | 4 | 178585.0022 | 1391547.1723 | 1570132.1745 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.066349 | 308.15 | 1 | 66559.8093 | 352782.2746 | 419342.0839 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.066349 | 308.15 | 2 | 94247.3114 | 705564.5492 | 799811.8606 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.066349 | 308.15 | 3 | 137085.3592 | 1058346.8239 | 1195432.1831 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.066349 | 308.15 | 4 | 195073.9529 | 1411129.0985 | 1606203.0513 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.066349 | 319.2611 | 1 | 66993.6897 | 373025.9988 | 440019.6885 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.066349 | 319.2611 | 2 | 94861.6771 | 746051.9976 | 840913.6747 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.066349 | 319.2611 | 3 | 137978.9714 | 1119077.9964 | 1257056.9678 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.066349 | 319.2611 | 4 | 196345.5727 | 1492103.9952 | 1688449.5679 | 0 | 0 | NORMAL
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on J3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).
Note on K3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation