## RS0001
RS0001: Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 3.0.0 |  | ✓
| description | ASHRAE 90.1-2022 Appendix J curve set 'J': 400.0+ ton, 6.28 COP, 7.03 IPLV liquid-cooled, centrifugal compressor chiller |  | ✓
| id | 7cfd3c29-f3c6-4c14-85cd-2db085cff1dd |  | ✓
| data_timestamp | 2025-02-18T13:40Z |  | ✓
| data_version | 3 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2022 Appendix J curve set 'J' for Energy Cost Budget (ECB) Path A
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | CENTRIFUGAL
performance |  |  |  | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| cycling_degradation_coefficient | 0 | - | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
performance.performance_map_evaporator_liquid_pressure_differential |  | $performance_map_evaporator_liqu |  | ✓
| condenser_type | LIQUID |  | ✓
performance.condenser_liquid_type
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| condenser_fouling_factor | 0 | m2-K/W
performance.performance_map_condenser_liquid_pressure_differential |  | $performance_map_condenser_liqui
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
performance.scaling
| minimum | 0.88889 | -
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on B20: Type of compressor speed control
Note on B21: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A22: Type of liquid in evaporator
Note on A23: An array of all liquid components within the liquid mixture
Note on B24: Defines whether concentration is defined on a volume or mass basis
Note on B25: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on A26: Data group describing the liquid pressure differential through the evaporator
Note on B27: Heat rejection method of the condenser
Note on A28: Type of liquid in condenser
Note on A29: An array of all liquid components within the liquid mixture
Note on B30: Defines whether concentration is defined on a volume or mass basis
Note on B31: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on A32: Data group describing the liquid pressure differential through the condenser
Note on A33: Data group describing cooling performance over a range of conditions
Note on A34: Data group describing standby performance
Note on A35: Specifies the range the performance data can be scaled to represent different capacity equipment
Note on B36: Minimum scaling factor

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_evaporator_liqu
performance.performance_map_evaporator_liquid_pressure_differential
grid_variables |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | evaporator_liquid_differential_pressure
m3/s | K | Pa
0.067809 | 275.3722 | 15000
0.067809 | 281.6685 | 15000
0.067809 | 287.9648 | 15000
0.067809 | 294.2611 | 15000
Note on A2: Data group defining the grid variables for the evaporator liquid pressure differential
Note on C2: Data group defining the lookup variables for the evaporator liquid pressure differential
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Pressure difference across the evaporator

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_condenser_liqui
performance.performance_map_condenser_liquid_pressure_differential
grid_variables |  | lookup_variables
condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | condenser_liquid_differential_pressure
m3/s | K | Pa
0.085306 | 285.9278 | 15000
0.085306 | 297.0389 | 15000
0.085306 | 308.15 | 15000
0.085306 | 319.2611 | 15000
Note on A2: Data group defining the grid variables for the condenser liquid pressure differential
Note on C2: Data group defining the lookup variables for the condenser liquid pressure differential
Note on A3: Condenser liquid flow
Note on B3: Entering condenser liquid temperature
Note on C3: Pressure difference across the condenser

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | oil_cooler_heat | auxiliary_heat | operation_state
m3/s | K | m3/s | K | - | W | W | W | W | W | -
0.067809 | 275.3722 | 0.085306 | 285.9278 | 1 | 66370.4293 | 370243.1871 | 436613.6164 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.085306 | 285.9278 | 2 | 92550.5318 | 740486.3742 | 833036.9061 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.085306 | 285.9278 | 3 | 134287.8456 | 1110729.5613 | 1245017.4069 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.085306 | 285.9278 | 4 | 191582.3706 | 1480972.7485 | 1672555.1191 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.085306 | 297.0389 | 1 | 74969.5143 | 333573.1528 | 408542.6671 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.085306 | 297.0389 | 2 | 104541.563 | 667146.3056 | 771687.8686 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.085306 | 297.0389 | 3 | 151686.4462 | 1000719.4584 | 1152405.9046 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.085306 | 297.0389 | 4 | 216404.164 | 1334292.6112 | 1550696.7751 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.085306 | 308.15 | 1 | 70013.8099 | 286645.6296 | 356659.4395 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.085306 | 308.15 | 2 | 97631.0596 | 573291.2591 | 670922.3188 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.085306 | 308.15 | 3 | 141659.5281 | 859936.8887 | 1001596.4168 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.085306 | 308.15 | 4 | 202099.2152 | 1146582.5183 | 1348681.7335 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.085306 | 319.2611 | 1 | 54560.5976 | 229460.6175 | 284021.215 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.085306 | 319.2611 | 2 | 76082.2609 | 458921.2349 | 535003.4959 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.085306 | 319.2611 | 3 | 110392.9141 | 688381.8524 | 798774.7665 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.085306 | 319.2611 | 4 | 157492.557 | 917842.4699 | 1075335.0269 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.085306 | 285.9278 | 1 | 71252.1343 | 458478.3833 | 529730.5177 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.085306 | 285.9278 | 2 | 99357.8465 | 916956.7667 | 1016314.6131 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.085306 | 285.9278 | 3 | 144165.0402 | 1375435.15 | 1519600.1902 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.085306 | 285.9278 | 4 | 205673.7157 | 1833913.5333 | 2039587.249 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.085306 | 297.0389 | 1 | 87996.8766 | 434817.45 | 522814.3266 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.085306 | 297.0389 | 2 | 122707.6247 | 869634.9 | 992342.5247 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.085306 | 297.0389 | 3 | 178044.8176 | 1304452.35 | 1482497.1676 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.085306 | 297.0389 | 4 | 254008.4554 | 1739269.8 | 1993278.2553 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.085306 | 308.15 | 1 | 89546.1485 | 400899.0278 | 490445.1763 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.085306 | 308.15 | 2 | 124868.0136 | 801798.0555 | 926666.0691 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.085306 | 308.15 | 3 | 181179.4724 | 1202697.0833 | 1383876.5557 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.085306 | 308.15 | 4 | 258480.525 | 1603596.111 | 1862076.636 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.085306 | 319.2611 | 1 | 77897.7207 | 356723.1166 | 434620.8373 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.085306 | 319.2611 | 2 | 108624.813 | 713446.2333 | 822071.0463 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.085306 | 319.2611 | 3 | 157611.1107 | 1070169.3499 | 1227780.4607 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.085306 | 319.2611 | 4 | 224856.6138 | 1426892.4666 | 1651749.0803 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.085306 | 285.9278 | 1 | 69371.3109 | 466909.6647 | 536280.9756 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.085306 | 285.9278 | 2 | 96735.1241 | 933819.3294 | 1030554.4535 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.085306 | 285.9278 | 3 | 140359.5544 | 1400728.9941 | 1541088.5486 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.085306 | 285.9278 | 4 | 200244.6019 | 1867638.6589 | 2067883.2607 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.085306 | 297.0389 | 1 | 89893.503 | 456257.8324 | 546151.3353 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.085306 | 297.0389 | 2 | 125352.3835 | 912515.6647 | 1037868.0482 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.085306 | 297.0389 | 3 | 181882.2775 | 1368773.4971 | 1550655.7746 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.085306 | 297.0389 | 4 | 259483.1852 | 1825031.3295 | 2084514.5146 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.085306 | 308.15 | 1 | 95555.3721 | 435348.5111 | 530903.8833 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.085306 | 308.15 | 2 | 133247.6014 | 870697.0222 | 1003944.6236 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.085306 | 308.15 | 3 | 193337.9848 | 1306045.5334 | 1499383.5182 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.085306 | 308.15 | 4 | 275826.5225 | 1741394.0445 | 2017220.567 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.085306 | 319.2611 | 1 | 87295.1785 | 404181.701 | 491476.8795 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.085306 | 319.2611 | 2 | 121729.1387 | 808363.402 | 930092.5407 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.085306 | 319.2611 | 3 | 176625.0659 | 1212545.103 | 1389170.1689 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.085306 | 319.2611 | 4 | 251982.96 | 1616726.804 | 1868709.764 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.085306 | 285.9278 | 1 | 62794.6649 | 395537.0313 | 458331.6962 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.085306 | 285.9278 | 2 | 87564.2917 | 791074.0626 | 878638.3543 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.085306 | 285.9278 | 3 | 127052.9716 | 1186611.0938 | 1313664.0654 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.085306 | 285.9278 | 4 | 181260.7044 | 1582148.1251 | 1763408.8295 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.085306 | 297.0389 | 1 | 83035.5552 | 397894.2999 | 480929.8551 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.085306 | 297.0389 | 2 | 115789.2885 | 795788.5998 | 911577.8884 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.085306 | 297.0389 | 3 | 168006.5343 | 1193682.8997 | 1361689.434 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.085306 | 297.0389 | 4 | 239687.2925 | 1591577.1997 | 1831264.4921 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.085306 | 308.15 | 1 | 90727.0987 | 389994.0797 | 480721.1783 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.085306 | 308.15 | 2 | 126514.7946 | 779988.1593 | 906502.9539 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.085306 | 308.15 | 3 | 183568.8987 | 1169982.239 | 1353551.1377 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.085306 | 308.15 | 4 | 261889.411 | 1559976.3186 | 1821865.7296 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.085306 | 319.2611 | 1 | 85748.0449 | 371836.3705 | 457584.4155 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.085306 | 319.2611 | 2 | 119571.7316 | 743672.741 | 863244.4727 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.085306 | 319.2611 | 3 | 173494.7376 | 1115509.1116 | 1289003.8491 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.085306 | 319.2611 | 4 | 247517.0628 | 1487345.4821 | 1734862.5449 | 0 | 0 | NORMAL
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on J3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).
Note on K3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation