## RS0001
RS0001: Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 3.0.0 |  | ✓
| description | ASHRAE 90.1-2022 Appendix J curve set 'K': 0.0-150.0 ton, 2.84 COP, 4.63 IPLV air-cooled, compressor chiller |  | ✓
| id | 8e91c8b5-073d-47a3-85fb-9cd37d46897d |  | ✓
| data_timestamp | 2025-02-18T13:40Z |  | ✓
| data_version | 3 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2022 Appendix J curve set 'K' for Energy Cost Budget (ECB) Path B
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
performance |  |  |  | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| cycling_degradation_coefficient | 0 | - | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
performance.performance_map_evaporator_liquid_pressure_differential |  | $performance_map_evaporator_liqu |  | ✓
| condenser_type | AIR |  | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
performance.scaling
| maximum | 2 | -
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on A18: Data group containing performance information
Note on B19: Type of compressor speed control
Note on B20: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A21: Type of liquid in evaporator
Note on A22: An array of all liquid components within the liquid mixture
Note on B23: Defines whether concentration is defined on a volume or mass basis
Note on B24: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on A25: Data group describing the liquid pressure differential through the evaporator
Note on B26: Heat rejection method of the condenser
Note on A27: Data group describing cooling performance over a range of conditions
Note on A28: Data group describing standby performance
Note on A29: Specifies the range the performance data can be scaled to represent different capacity equipment
Note on B30: Maximum scaling factor

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_evaporator_liqu
performance.performance_map_evaporator_liquid_pressure_differential
grid_variables |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | evaporator_liquid_differential_pressure
m3/s | K | Pa
0.011302 | 275.3722 | 15000
0.011302 | 281.6685 | 15000
0.011302 | 287.9648 | 15000
0.011302 | 294.2611 | 15000
Note on A2: Data group defining the grid variables for the evaporator liquid pressure differential
Note on C2: Data group defining the lookup variables for the evaporator liquid pressure differential
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Pressure difference across the evaporator

## performance_map_cooling
performance.performance_map_cooling
grid_variables | [5 empty] | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_air_entering_drybulb_temperature | condenser_air_entering_relative_humidity | ambient_pressure | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | condenser_air_volumetric_flow_rate | oil_cooler_heat | auxiliary_heat | operation_state
m3/s | K | K | - | Pa | - | W | W | W | m3/s | W | W | -
0.011302 | 275.3722 | 285.9278 | 0.4 | 101325 | 1 | 10434.7564 | 60562.6892 | 70997.4457 | 7.9689 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 285.9278 | 0.4 | 101325 | 2 | 27409.5567 | 121125.3784 | 148534.9351 | 15.9378 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 285.9278 | 0.4 | 101325 | 3 | 48628.4977 | 181688.0677 | 230316.5654 | 23.9067 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 285.9278 | 0.4 | 101325 | 4 | 69253.3443 | 242250.7569 | 311504.1012 | 31.8756 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 299.0019 | 0.4 | 101325 | 1 | 12005.0465 | 60075.4651 | 72080.5117 | 7.9689 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 299.0019 | 0.4 | 101325 | 2 | 31534.3253 | 120150.9302 | 151685.2555 | 15.9378 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 299.0019 | 0.4 | 101325 | 3 | 55946.4308 | 180226.3953 | 236172.8261 | 23.9067 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 299.0019 | 0.4 | 101325 | 4 | 79675.0387 | 240301.8604 | 319976.8991 | 31.8756 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 312.0759 | 0.4 | 101325 | 1 | 13845.6833 | 53186.0924 | 67031.7757 | 7.9689 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 312.0759 | 0.4 | 101325 | 2 | 36369.2284 | 106372.1849 | 142741.4133 | 15.9378 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 312.0759 | 0.4 | 101325 | 3 | 64524.2446 | 159558.2773 | 224082.5219 | 23.9067 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 312.0759 | 0.4 | 101325 | 4 | 91890.9681 | 212744.3697 | 304635.3378 | 31.8756 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 325.15 | 0.4 | 101325 | 1 | 14113.672 | 39894.5712 | 54008.2432 | 7.9689 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 325.15 | 0.4 | 101325 | 2 | 37073.1693 | 79789.1424 | 116862.3118 | 15.9378 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 325.15 | 0.4 | 101325 | 3 | 65773.1371 | 119683.7136 | 185456.8507 | 23.9067 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 325.15 | 0.4 | 101325 | 4 | 93669.5544 | 159578.2848 | 253247.8392 | 31.8756 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 285.9278 | 0.4 | 101325 | 1 | 11161.506 | 75339.7363 | 86501.2422 | 7.9689 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 285.9278 | 0.4 | 101325 | 2 | 29318.5503 | 150679.4725 | 179998.0228 | 15.9378 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 285.9278 | 0.4 | 101325 | 3 | 52015.327 | 226019.2088 | 278034.5358 | 23.9067 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 285.9278 | 0.4 | 101325 | 4 | 74076.6325 | 301358.945 | 375435.5776 | 31.8756 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 299.0019 | 0.4 | 101325 | 1 | 12547.8334 | 73647.4634 | 86195.2969 | 7.9689 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 299.0019 | 0.4 | 101325 | 2 | 32960.0939 | 147294.9269 | 180255.0208 | 15.9378 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 299.0019 | 0.4 | 101325 | 3 | 58475.9494 | 220942.3903 | 279418.3397 | 23.9067 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 299.0019 | 0.4 | 101325 | 4 | 83277.4042 | 294589.8537 | 377867.258 | 31.8756 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 312.0759 | 0.4 | 101325 | 1 | 14786.2423 | 65553.0421 | 80339.2844 | 7.9689 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 312.0759 | 0.4 | 101325 | 2 | 38839.8474 | 131106.0841 | 169945.9315 | 15.9378 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 312.0759 | 0.4 | 101325 | 3 | 68907.4781 | 196659.1262 | 265566.6043 | 23.9067 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 312.0759 | 0.4 | 101325 | 4 | 98133.2663 | 262212.1682 | 360345.4345 | 31.8756 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 325.15 | 0.4 | 101325 | 1 | 16016.5431 | 51056.4721 | 67073.0152 | 7.9689 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 325.15 | 0.4 | 101325 | 2 | 42071.547 | 102112.9442 | 144184.4912 | 15.9378 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 325.15 | 0.4 | 101325 | 3 | 74640.9782 | 153169.4164 | 227810.3946 | 23.9067 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 325.15 | 0.4 | 101325 | 4 | 106298.5207 | 204225.8885 | 310524.4091 | 31.8756 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 285.9278 | 0.4 | 101325 | 1 | 11863.8864 | 79827.5993 | 91691.4857 | 7.9689 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 285.9278 | 0.4 | 101325 | 2 | 31163.532 | 159655.1986 | 190818.7306 | 15.9378 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 285.9278 | 0.4 | 101325 | 3 | 55288.59 | 239482.7979 | 294771.388 | 23.9067 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 285.9278 | 0.4 | 101325 | 4 | 78738.1874 | 319310.3972 | 398048.5846 | 31.8756 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 299.0019 | 0.4 | 101325 | 1 | 12734.9513 | 76930.2778 | 89665.2291 | 7.9689 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 299.0019 | 0.4 | 101325 | 2 | 33451.6068 | 153860.5555 | 187312.1624 | 15.9378 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 299.0019 | 0.4 | 101325 | 3 | 59347.964 | 230790.8333 | 290138.7974 | 23.9067 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 299.0019 | 0.4 | 101325 | 4 | 84519.2672 | 307721.1111 | 392240.3783 | 31.8756 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 312.0759 | 0.4 | 101325 | 1 | 14568.7167 | 67630.8077 | 82199.5244 | 7.9689 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 312.0759 | 0.4 | 101325 | 2 | 38268.4607 | 135261.6154 | 173530.0761 | 15.9378 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 312.0759 | 0.4 | 101325 | 3 | 67893.7559 | 202892.4231 | 270786.1789 | 23.9067 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 312.0759 | 0.4 | 101325 | 4 | 96689.5931 | 270523.2307 | 367212.8239 | 31.8756 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 325.15 | 0.4 | 101325 | 1 | 15487.7979 | 51929.189 | 67416.987 | 7.9689 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 325.15 | 0.4 | 101325 | 2 | 40682.6626 | 103858.3781 | 144541.0407 | 15.9378 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 325.15 | 0.4 | 101325 | 3 | 72176.8975 | 155787.5671 | 227964.4647 | 23.9067 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 325.15 | 0.4 | 101325 | 4 | 102789.3473 | 207716.7562 | 310506.1035 | 31.8756 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 285.9278 | 0.4 | 101325 | 1 | 12858.836 | 74026.2784 | 86885.1144 | 7.9689 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 285.9278 | 0.4 | 101325 | 2 | 33777.0217 | 148052.5568 | 181829.5785 | 15.9378 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 285.9278 | 0.4 | 101325 | 3 | 59925.2968 | 222078.8351 | 282004.132 | 23.9067 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 285.9278 | 0.4 | 101325 | 4 | 85341.4647 | 296105.1135 | 381446.5782 | 31.8756 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 299.0019 | 0.4 | 101325 | 1 | 12958.1867 | 69923.9081 | 82882.0948 | 7.9689 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 299.0019 | 0.4 | 101325 | 2 | 34037.9917 | 139847.8163 | 173885.808 | 15.9378 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 299.0019 | 0.4 | 101325 | 3 | 60388.2952 | 209771.7244 | 270160.0196 | 23.9067 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 299.0019 | 0.4 | 101325 | 4 | 86000.835 | 279695.6325 | 365696.4675 | 31.8756 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 312.0759 | 0.4 | 101325 | 1 | 13659.741 | 59419.3893 | 73079.1304 | 7.9689 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 312.0759 | 0.4 | 101325 | 2 | 35880.8037 | 118838.7787 | 154719.5823 | 15.9378 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 312.0759 | 0.4 | 101325 | 3 | 63657.7088 | 178258.168 | 241915.8768 | 23.9067 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 312.0759 | 0.4 | 101325 | 4 | 90656.9077 | 237677.5573 | 328334.465 | 31.8756 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 325.15 | 0.4 | 101325 | 1 | 13068.9194 | 42512.722 | 55581.6413 | 7.9689 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 325.15 | 0.4 | 101325 | 2 | 34328.8594 | 85025.444 | 119354.3034 | 15.9378 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 325.15 | 0.4 | 101325 | 3 | 60904.3363 | 127538.1659 | 188442.5023 | 23.9067 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 325.15 | 0.4 | 101325 | 4 | 86735.745 | 170050.8879 | 256786.633 | 31.8756 | 0 | 0 | NORMAL
Note on A2: Data group defining the grid variables for cooling performance
Note on G2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Entering condenser air drybulb temperature
Note on D3: Entering condenser air relative humidity
Note on E3: Ambient pressure used to calculate the performance
Note on F3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on G3: Total power input
Note on H3: Refrigeration capacity
Note on I3: Condenser heat rejection
Note on J3: Condenser air flow
Note on K3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on L3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).
Note on M3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation