## RS0001
RS0001: Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 3.0.0 |  | ✓
| description | ASHRAE 90.1-2022 Appendix J curve set 'L': 150.0+ ton, 2.84 COP, 4.72 IPLV air-cooled, compressor chiller |  | ✓
| id | 94e04b83-ace8-4fc3-8082-7c046896acbe |  | ✓
| data_timestamp | 2025-02-18T13:40Z |  | ✓
| data_version | 3 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2022 Appendix J curve set 'L' for Energy Cost Budget (ECB) Path B
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
performance |  |  |  | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| cycling_degradation_coefficient | 0 | - | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
performance.performance_map_evaporator_liquid_pressure_differential |  | $performance_map_evaporator_liqu |  | ✓
| condenser_type | AIR |  | ✓
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
performance.scaling
| minimum | 0.75 | -
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on A18: Data group containing performance information
Note on B19: Type of compressor speed control
Note on B20: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A21: Type of liquid in evaporator
Note on A22: An array of all liquid components within the liquid mixture
Note on B23: Defines whether concentration is defined on a volume or mass basis
Note on B24: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on A25: Data group describing the liquid pressure differential through the evaporator
Note on B26: Heat rejection method of the condenser
Note on A27: Data group describing cooling performance over a range of conditions
Note on A28: Data group describing standby performance
Note on A29: Specifies the range the performance data can be scaled to represent different capacity equipment
Note on B30: Minimum scaling factor

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_evaporator_liqu
performance.performance_map_evaporator_liquid_pressure_differential
grid_variables |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | evaporator_liquid_differential_pressure
m3/s | K | Pa
0.030137 | 275.3722 | 15000
0.030137 | 281.6685 | 15000
0.030137 | 287.9648 | 15000
0.030137 | 294.2611 | 15000
Note on A2: Data group defining the grid variables for the evaporator liquid pressure differential
Note on C2: Data group defining the lookup variables for the evaporator liquid pressure differential
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Pressure difference across the evaporator

## performance_map_cooling
performance.performance_map_cooling
grid_variables | [5 empty] | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_air_entering_drybulb_temperature | condenser_air_entering_relative_humidity | ambient_pressure | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | condenser_air_volumetric_flow_rate | oil_cooler_heat | auxiliary_heat | operation_state
m3/s | K | K | - | Pa | - | W | W | W | m3/s | W | W | -
0.030137 | 275.3722 | 285.9278 | 0.4 | 101325 | 1 | 32544.8512 | 173443.0851 | 205987.9362 | 21.2274 | 0 | 0 | NORMAL
0.030137 | 275.3722 | 285.9278 | 0.4 | 101325 | 2 | 71541.0332 | 346886.1701 | 418427.2034 | 42.4547 | 0 | 0 | NORMAL
0.030137 | 275.3722 | 285.9278 | 0.4 | 101325 | 3 | 123174.9066 | 520329.2552 | 643504.1618 | 63.6821 | 0 | 0 | NORMAL
0.030137 | 275.3722 | 285.9278 | 0.4 | 101325 | 4 | 176753.9045 | 693772.3403 | 870526.2448 | 84.9095 | 0 | 0 | NORMAL
0.030137 | 275.3722 | 299.0019 | 0.4 | 101325 | 1 | 38170.7278 | 160951.1938 | 199121.9216 | 21.2274 | 0 | 0 | NORMAL
0.030137 | 275.3722 | 299.0019 | 0.4 | 101325 | 2 | 83907.998 | 321902.3876 | 405810.3856 | 42.4547 | 0 | 0 | NORMAL
0.030137 | 275.3722 | 299.0019 | 0.4 | 101325 | 3 | 144467.5782 | 482853.5814 | 627321.1597 | 63.6821 | 0 | 0 | NORMAL
0.030137 | 275.3722 | 299.0019 | 0.4 | 101325 | 4 | 207308.5277 | 643804.7752 | 851113.3029 | 84.9095 | 0 | 0 | NORMAL
0.030137 | 275.3722 | 312.0759 | 0.4 | 101325 | 1 | 44229.3375 | 139081.5075 | 183310.8449 | 21.2274 | 0 | 0 | NORMAL
0.030137 | 275.3722 | 312.0759 | 0.4 | 101325 | 2 | 97226.209 | 278163.015 | 375389.224 | 42.4547 | 0 | 0 | NORMAL
0.030137 | 275.3722 | 312.0759 | 0.4 | 101325 | 3 | 167398.0466 | 417244.5225 | 584642.569 | 63.6821 | 0 | 0 | NORMAL
0.030137 | 275.3722 | 312.0759 | 0.4 | 101325 | 4 | 240213.3613 | 556326.0299 | 796539.3913 | 84.9095 | 0 | 0 | NORMAL
0.030137 | 275.3722 | 325.15 | 0.4 | 101325 | 1 | 46390.0965 | 107834.0261 | 154224.1226 | 21.2274 | 0 | 0 | NORMAL
0.030137 | 275.3722 | 325.15 | 0.4 | 101325 | 2 | 101976.052 | 215668.0522 | 317644.1042 | 42.4547 | 0 | 0 | NORMAL
0.030137 | 275.3722 | 325.15 | 0.4 | 101325 | 3 | 175576.0312 | 323502.0783 | 499078.1095 | 63.6821 | 0 | 0 | NORMAL
0.030137 | 275.3722 | 325.15 | 0.4 | 101325 | 4 | 251948.6308 | 431336.1044 | 683284.7352 | 84.9095 | 0 | 0 | NORMAL
0.030137 | 281.6685 | 285.9278 | 0.4 | 101325 | 1 | 33901.664 | 214427.1865 | 248328.8505 | 21.2274 | 0 | 0 | NORMAL
0.030137 | 281.6685 | 285.9278 | 0.4 | 101325 | 2 | 74523.6184 | 428854.3729 | 503377.9913 | 42.4547 | 0 | 0 | NORMAL
0.030137 | 281.6685 | 285.9278 | 0.4 | 101325 | 3 | 128310.1365 | 643281.5594 | 771591.6959 | 63.6821 | 0 | 0 | NORMAL
0.030137 | 281.6685 | 285.9278 | 0.4 | 101325 | 4 | 184122.8725 | 857708.7458 | 1041831.6183 | 84.9095 | 0 | 0 | NORMAL
0.030137 | 281.6685 | 299.0019 | 0.4 | 101325 | 1 | 40299.0825 | 199691.661 | 239990.7435 | 21.2274 | 0 | 0 | NORMAL
0.030137 | 281.6685 | 299.0019 | 0.4 | 101325 | 2 | 88586.6088 | 399383.3219 | 487969.9308 | 42.4547 | 0 | 0 | NORMAL
0.030137 | 281.6685 | 299.0019 | 0.4 | 101325 | 3 | 152522.9198 | 599074.9829 | 751597.9026 | 63.6821 | 0 | 0 | NORMAL
0.030137 | 281.6685 | 299.0019 | 0.4 | 101325 | 4 | 218867.8063 | 798766.6439 | 1017634.4502 | 84.9095 | 0 | 0 | NORMAL
0.030137 | 281.6685 | 312.0759 | 0.4 | 101325 | 1 | 48608.0758 | 175578.3404 | 224186.4162 | 21.2274 | 0 | 0 | NORMAL
0.030137 | 281.6685 | 312.0759 | 0.4 | 101325 | 2 | 106851.6783 | 351156.6808 | 458008.3591 | 42.4547 | 0 | 0 | NORMAL
0.030137 | 281.6685 | 312.0759 | 0.4 | 101325 | 3 | 183970.5816 | 526735.0212 | 710705.6028 | 63.6821 | 0 | 0 | NORMAL
0.030137 | 281.6685 | 312.0759 | 0.4 | 101325 | 4 | 263994.6684 | 702313.3616 | 966308.0301 | 84.9095 | 0 | 0 | NORMAL
0.030137 | 281.6685 | 325.15 | 0.4 | 101325 | 1 | 54450.7111 | 142087.2248 | 196537.9359 | 21.2274 | 0 | 0 | NORMAL
0.030137 | 281.6685 | 325.15 | 0.4 | 101325 | 2 | 119695.1282 | 284174.4496 | 403869.5777 | 42.4547 | 0 | 0 | NORMAL
0.030137 | 281.6685 | 325.15 | 0.4 | 101325 | 3 | 206083.6358 | 426261.6743 | 632345.3101 | 63.6821 | 0 | 0 | NORMAL
0.030137 | 281.6685 | 325.15 | 0.4 | 101325 | 4 | 295726.5266 | 568348.8991 | 864075.4257 | 84.9095 | 0 | 0 | NORMAL
0.030137 | 287.9648 | 285.9278 | 0.4 | 101325 | 1 | 35776.8463 | 227610.9723 | 263387.8186 | 21.2274 | 0 | 0 | NORMAL
0.030137 | 287.9648 | 285.9278 | 0.4 | 101325 | 2 | 78645.6983 | 455221.9446 | 533867.6429 | 42.4547 | 0 | 0 | NORMAL
0.030137 | 287.9648 | 285.9278 | 0.4 | 101325 | 3 | 135407.2776 | 682832.9169 | 818240.1945 | 63.6821 | 0 | 0 | NORMAL
0.030137 | 287.9648 | 285.9278 | 0.4 | 101325 | 4 | 194307.1498 | 910443.8892 | 1104751.039 | 84.9095 | 0 | 0 | NORMAL
0.030137 | 287.9648 | 299.0019 | 0.4 | 101325 | 1 | 41088.6388 | 210631.8126 | 251720.4513 | 21.2274 | 0 | 0 | NORMAL
0.030137 | 287.9648 | 299.0019 | 0.4 | 101325 | 2 | 90322.2342 | 421263.6251 | 511585.8594 | 42.4547 | 0 | 0 | NORMAL
0.030137 | 287.9648 | 299.0019 | 0.4 | 101325 | 3 | 155511.2117 | 631895.4377 | 787406.6494 | 63.6821 | 0 | 0 | NORMAL
0.030137 | 287.9648 | 299.0019 | 0.4 | 101325 | 4 | 223155.9547 | 842527.2503 | 1065683.205 | 84.9095 | 0 | 0 | NORMAL
0.030137 | 287.9648 | 312.0759 | 0.4 | 101325 | 1 | 48703.5127 | 184274.8578 | 232978.3705 | 21.2274 | 0 | 0 | NORMAL
0.030137 | 287.9648 | 312.0759 | 0.4 | 101325 | 2 | 107061.4704 | 368549.7156 | 475611.186 | 42.4547 | 0 | 0 | NORMAL
0.030137 | 287.9648 | 312.0759 | 0.4 | 101325 | 3 | 184331.7887 | 552824.5733 | 737156.362 | 63.6821 | 0 | 0 | NORMAL
0.030137 | 287.9648 | 312.0759 | 0.4 | 101325 | 4 | 264512.9944 | 737099.4311 | 1001612.4256 | 84.9095 | 0 | 0 | NORMAL
0.030137 | 287.9648 | 325.15 | 0.4 | 101325 | 1 | 54196.1861 | 148540.1079 | 202736.294 | 21.2274 | 0 | 0 | NORMAL
0.030137 | 287.9648 | 325.15 | 0.4 | 101325 | 2 | 119135.624 | 297080.2158 | 416215.8398 | 42.4547 | 0 | 0 | NORMAL
0.030137 | 287.9648 | 325.15 | 0.4 | 101325 | 3 | 205120.3162 | 445620.3238 | 650740.64 | 63.6821 | 0 | 0 | NORMAL
0.030137 | 287.9648 | 325.15 | 0.4 | 101325 | 4 | 294344.1793 | 594160.4317 | 888504.611 | 84.9095 | 0 | 0 | NORMAL
0.030137 | 294.2611 | 285.9278 | 0.4 | 101325 | 1 | 39378.9154 | 212994.4426 | 252373.358 | 21.2274 | 0 | 0 | NORMAL
0.030137 | 294.2611 | 285.9278 | 0.4 | 101325 | 2 | 86563.8709 | 425988.8852 | 512552.7561 | 42.4547 | 0 | 0 | NORMAL
0.030137 | 294.2611 | 285.9278 | 0.4 | 101325 | 3 | 149040.2952 | 638983.3278 | 788023.623 | 63.6821 | 0 | 0 | NORMAL
0.030137 | 294.2611 | 285.9278 | 0.4 | 101325 | 4 | 213870.2991 | 851977.7704 | 1065848.0695 | 84.9095 | 0 | 0 | NORMAL
0.030137 | 294.2611 | 299.0019 | 0.4 | 101325 | 1 | 42040.1914 | 193771.6486 | 235811.8401 | 21.2274 | 0 | 0 | NORMAL
0.030137 | 294.2611 | 299.0019 | 0.4 | 101325 | 2 | 92413.9648 | 387543.2973 | 479957.2621 | 42.4547 | 0 | 0 | NORMAL
0.030137 | 294.2611 | 299.0019 | 0.4 | 101325 | 3 | 159112.6235 | 581314.9459 | 740427.5695 | 63.6821 | 0 | 0 | NORMAL
0.030137 | 294.2611 | 299.0019 | 0.4 | 101325 | 4 | 228323.9197 | 775086.5946 | 1003410.5142 | 84.9095 | 0 | 0 | NORMAL
0.030137 | 294.2611 | 312.0759 | 0.4 | 101325 | 1 | 46308.7205 | 165171.0596 | 211479.7801 | 21.2274 | 0 | 0 | NORMAL
0.030137 | 294.2611 | 312.0759 | 0.4 | 101325 | 2 | 101797.1688 | 330342.1192 | 432139.2881 | 42.4547 | 0 | 0 | NORMAL
0.030137 | 294.2611 | 312.0759 | 0.4 | 101325 | 3 | 175268.0413 | 495513.1788 | 670781.2201 | 63.6821 | 0 | 0 | NORMAL
0.030137 | 294.2611 | 312.0759 | 0.4 | 101325 | 4 | 251506.6704 | 660684.2385 | 912190.9089 | 84.9095 | 0 | 0 | NORMAL
0.030137 | 294.2611 | 325.15 | 0.4 | 101325 | 1 | 47711.8713 | 127192.6755 | 174904.5468 | 21.2274 | 0 | 0 | NORMAL
0.030137 | 294.2611 | 325.15 | 0.4 | 101325 | 2 | 104881.6156 | 254385.3511 | 359266.9667 | 42.4547 | 0 | 0 | NORMAL
0.030137 | 294.2611 | 325.15 | 0.4 | 101325 | 3 | 180578.6501 | 381578.0266 | 562156.6767 | 63.6821 | 0 | 0 | NORMAL
0.030137 | 294.2611 | 325.15 | 0.4 | 101325 | 4 | 259127.3042 | 508770.7021 | 767898.0063 | 84.9095 | 0 | 0 | NORMAL
Note on A2: Data group defining the grid variables for cooling performance
Note on G2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Entering condenser air drybulb temperature
Note on D3: Entering condenser air relative humidity
Note on E3: Ambient pressure used to calculate the performance
Note on F3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on G3: Total power input
Note on H3: Refrigeration capacity
Note on I3: Condenser heat rejection
Note on J3: Condenser air flow
Note on K3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on L3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).
Note on M3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation