## RS0001
RS0001: Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 3.0.0 |  | ✓
| description | ASHRAE 90.1-2022 Appendix J curve set 'M': 0.0-75.0 ton, 4.51 COP, 7.03 IPLV liquid-cooled, positive displacement compressor chiller |  | ✓
| id | 55279f6c-9476-425e-8e77-0e57cc5f7dbf |  | ✓
| data_timestamp | 2025-02-18T13:40Z |  | ✓
| data_version | 3 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2022 Appendix J curve set 'M' for Energy Cost Budget (ECB) Path B
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | SCROLL
performance |  |  |  | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| cycling_degradation_coefficient | 0 | - | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
performance.performance_map_evaporator_liquid_pressure_differential |  | $performance_map_evaporator_liqu |  | ✓
| condenser_type | LIQUID |  | ✓
performance.condenser_liquid_type
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| condenser_fouling_factor | 0 | m2-K/W
performance.performance_map_condenser_liquid_pressure_differential |  | $performance_map_condenser_liqui
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
performance.scaling
| maximum | 2 | -
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on B20: Type of compressor speed control
Note on B21: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A22: Type of liquid in evaporator
Note on A23: An array of all liquid components within the liquid mixture
Note on B24: Defines whether concentration is defined on a volume or mass basis
Note on B25: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on A26: Data group describing the liquid pressure differential through the evaporator
Note on B27: Heat rejection method of the condenser
Note on A28: Type of liquid in condenser
Note on A29: An array of all liquid components within the liquid mixture
Note on B30: Defines whether concentration is defined on a volume or mass basis
Note on B31: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on A32: Data group describing the liquid pressure differential through the condenser
Note on A33: Data group describing cooling performance over a range of conditions
Note on A34: Data group describing standby performance
Note on A35: Specifies the range the performance data can be scaled to represent different capacity equipment
Note on B36: Maximum scaling factor

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_evaporator_liqu
performance.performance_map_evaporator_liquid_pressure_differential
grid_variables |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | evaporator_liquid_differential_pressure
m3/s | K | Pa
0.0056508 | 275.3722 | 15000
0.0056508 | 281.6685 | 15000
0.0056508 | 287.9648 | 15000
0.0056508 | 294.2611 | 15000
Note on A2: Data group defining the grid variables for the evaporator liquid pressure differential
Note on C2: Data group defining the lookup variables for the evaporator liquid pressure differential
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Pressure difference across the evaporator

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_condenser_liqui
performance.performance_map_condenser_liquid_pressure_differential
grid_variables |  | lookup_variables
condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | condenser_liquid_differential_pressure
m3/s | K | Pa
0.0074924 | 285.9278 | 15000
0.0074924 | 297.0389 | 15000
0.0074924 | 308.15 | 15000
0.0074924 | 319.2611 | 15000
Note on A2: Data group defining the grid variables for the condenser liquid pressure differential
Note on C2: Data group defining the lookup variables for the condenser liquid pressure differential
Note on A3: Condenser liquid flow
Note on B3: Entering condenser liquid temperature
Note on C3: Pressure difference across the condenser

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | oil_cooler_heat | auxiliary_heat | operation_state
m3/s | K | m3/s | K | - | W | W | W | W | W | -
0.0056508 | 275.3722 | 0.0074924 | 285.9278 | 1 | 4406.9513 | 30843.0512 | 35250.0025 | 0 | 0 | NORMAL
0.0056508 | 275.3722 | 0.0074924 | 285.9278 | 2 | 8387.5391 | 61686.1024 | 70073.6415 | 0 | 0 | NORMAL
0.0056508 | 275.3722 | 0.0074924 | 285.9278 | 3 | 14340.7541 | 92529.1536 | 106869.9078 | 0 | 0 | NORMAL
0.0056508 | 275.3722 | 0.0074924 | 285.9278 | 4 | 22266.5966 | 123372.2049 | 145638.8014 | 0 | 0 | NORMAL
0.0056508 | 275.3722 | 0.0074924 | 297.0389 | 1 | 5014.6917 | 28825.2159 | 33839.9076 | 0 | 0 | NORMAL
0.0056508 | 275.3722 | 0.0074924 | 297.0389 | 2 | 9544.2222 | 57650.4318 | 67194.654 | 0 | 0 | NORMAL
0.0056508 | 275.3722 | 0.0074924 | 297.0389 | 3 | 16318.4151 | 86475.6477 | 102794.0628 | 0 | 0 | NORMAL
0.0056508 | 275.3722 | 0.0074924 | 297.0389 | 4 | 25337.2703 | 115300.8636 | 140638.134 | 0 | 0 | NORMAL
0.0056508 | 275.3722 | 0.0074924 | 308.15 | 1 | 5799.727 | 25374.5885 | 31174.3156 | 0 | 0 | NORMAL
0.0056508 | 275.3722 | 0.0074924 | 308.15 | 2 | 11038.3423 | 50749.177 | 61787.5193 | 0 | 0 | NORMAL
0.0056508 | 275.3722 | 0.0074924 | 308.15 | 3 | 18873.0153 | 76123.7655 | 94996.7809 | 0 | 0 | NORMAL
0.0056508 | 275.3722 | 0.0074924 | 308.15 | 4 | 29303.7461 | 101498.354 | 130802.1001 | 0 | 0 | NORMAL
0.0056508 | 275.3722 | 0.0074924 | 319.2611 | 1 | 6284.0164 | 20491.169 | 26775.1854 | 0 | 0 | NORMAL
0.0056508 | 275.3722 | 0.0074924 | 319.2611 | 2 | 11960.067 | 40982.338 | 52942.405 | 0 | 0 | NORMAL
0.0056508 | 275.3722 | 0.0074924 | 319.2611 | 3 | 20448.9515 | 61473.507 | 81922.4585 | 0 | 0 | NORMAL
0.0056508 | 275.3722 | 0.0074924 | 319.2611 | 4 | 31750.6701 | 81964.676 | 113715.3461 | 0 | 0 | NORMAL
0.0056508 | 281.6685 | 0.0074924 | 285.9278 | 1 | 4563.1028 | 38013.3109 | 42576.4137 | 0 | 0 | NORMAL
0.0056508 | 281.6685 | 0.0074924 | 285.9278 | 2 | 8684.7346 | 76026.6219 | 84711.3565 | 0 | 0 | NORMAL
0.0056508 | 281.6685 | 0.0074924 | 285.9278 | 3 | 14848.8899 | 114039.9328 | 128888.8227 | 0 | 0 | NORMAL
0.0056508 | 281.6685 | 0.0074924 | 285.9278 | 4 | 23055.5686 | 152053.2437 | 175108.8123 | 0 | 0 | NORMAL
0.0056508 | 281.6685 | 0.0074924 | 297.0389 | 1 | 5269.382 | 36039.3006 | 41308.6826 | 0 | 0 | NORMAL
0.0056508 | 281.6685 | 0.0074924 | 297.0389 | 2 | 10028.962 | 72078.6012 | 82107.5632 | 0 | 0 | NORMAL
0.0056508 | 281.6685 | 0.0074924 | 297.0389 | 3 | 17147.2081 | 108117.9018 | 125265.1099 | 0 | 0 | NORMAL
0.0056508 | 281.6685 | 0.0074924 | 297.0389 | 4 | 26624.1204 | 144157.2024 | 170781.3228 | 0 | 0 | NORMAL
0.0056508 | 281.6685 | 0.0074924 | 308.15 | 1 | 6392.5191 | 32632.4982 | 39025.0173 | 0 | 0 | NORMAL
0.0056508 | 281.6685 | 0.0074924 | 308.15 | 2 | 12166.5749 | 65264.9964 | 77431.5713 | 0 | 0 | NORMAL
0.0056508 | 281.6685 | 0.0074924 | 308.15 | 3 | 20802.0325 | 97897.4946 | 118699.5271 | 0 | 0 | NORMAL
0.0056508 | 281.6685 | 0.0074924 | 308.15 | 4 | 32298.8917 | 130529.9928 | 162828.8844 | 0 | 0 | NORMAL
0.0056508 | 281.6685 | 0.0074924 | 319.2611 | 1 | 7478.6832 | 27792.9037 | 35271.5869 | 0 | 0 | NORMAL
0.0056508 | 281.6685 | 0.0074924 | 319.2611 | 2 | 14233.8191 | 55585.8074 | 69819.6264 | 0 | 0 | NORMAL
0.0056508 | 281.6685 | 0.0074924 | 319.2611 | 3 | 24336.5424 | 83378.711 | 107715.2534 | 0 | 0 | NORMAL
0.0056508 | 281.6685 | 0.0074924 | 319.2611 | 4 | 37786.8532 | 111171.6147 | 148958.4679 | 0 | 0 | NORMAL
0.0056508 | 287.9648 | 0.0074924 | 285.9278 | 1 | 4715.9689 | 39644.2462 | 44360.2152 | 0 | 0 | NORMAL
0.0056508 | 287.9648 | 0.0074924 | 285.9278 | 2 | 8975.6775 | 79288.4925 | 88264.1699 | 0 | 0 | NORMAL
0.0056508 | 287.9648 | 0.0074924 | 285.9278 | 3 | 15346.3349 | 118932.7387 | 134279.0736 | 0 | 0 | NORMAL
0.0056508 | 287.9648 | 0.0074924 | 285.9278 | 4 | 23827.9413 | 158576.9849 | 182404.9263 | 0 | 0 | NORMAL
0.0056508 | 287.9648 | 0.0074924 | 297.0389 | 1 | 5288.1302 | 37714.0609 | 43002.1911 | 0 | 0 | NORMAL
0.0056508 | 287.9648 | 0.0074924 | 297.0389 | 2 | 10064.6445 | 75428.1218 | 85492.7663 | 0 | 0 | NORMAL
0.0056508 | 287.9648 | 0.0074924 | 297.0389 | 3 | 17208.217 | 113142.1827 | 130350.3997 | 0 | 0 | NORMAL
0.0056508 | 287.9648 | 0.0074924 | 297.0389 | 4 | 26718.8477 | 150856.2436 | 177575.0913 | 0 | 0 | NORMAL
0.0056508 | 287.9648 | 0.0074924 | 308.15 | 1 | 6354.4442 | 34351.0835 | 40705.5276 | 0 | 0 | NORMAL
0.0056508 | 287.9648 | 0.0074924 | 308.15 | 2 | 12094.1088 | 68702.1669 | 80796.2758 | 0 | 0 | NORMAL
0.0056508 | 287.9648 | 0.0074924 | 308.15 | 3 | 20678.1321 | 103053.2504 | 123731.3826 | 0 | 0 | NORMAL
0.0056508 | 287.9648 | 0.0074924 | 308.15 | 4 | 32106.5142 | 137404.3339 | 169510.848 | 0 | 0 | NORMAL
0.0056508 | 287.9648 | 0.0074924 | 319.2611 | 1 | 7485.2902 | 29555.3139 | 37040.6042 | 0 | 0 | NORMAL
0.0056508 | 287.9648 | 0.0074924 | 319.2611 | 2 | 14246.3939 | 59110.6279 | 73357.0218 | 0 | 0 | NORMAL
0.0056508 | 287.9648 | 0.0074924 | 319.2611 | 3 | 24358.0424 | 88665.9418 | 113023.9842 | 0 | 0 | NORMAL
0.0056508 | 287.9648 | 0.0074924 | 319.2611 | 4 | 37820.2358 | 118221.2558 | 156041.4916 | 0 | 0 | NORMAL
0.0056508 | 294.2611 | 0.0074924 | 285.9278 | 1 | 4990.0099 | 35735.8571 | 40725.8671 | 0 | 0 | NORMAL
0.0056508 | 294.2611 | 0.0074924 | 285.9278 | 2 | 9497.2466 | 71471.7143 | 80968.9608 | 0 | 0 | NORMAL
0.0056508 | 294.2611 | 0.0074924 | 285.9278 | 3 | 16238.0976 | 107207.5714 | 123445.669 | 0 | 0 | NORMAL
0.0056508 | 294.2611 | 0.0074924 | 285.9278 | 4 | 25212.5631 | 142943.4285 | 168155.9916 | 0 | 0 | NORMAL
0.0056508 | 294.2611 | 0.0074924 | 297.0389 | 1 | 5279.9066 | 33849.4968 | 39129.4034 | 0 | 0 | NORMAL
0.0056508 | 294.2611 | 0.0074924 | 297.0389 | 2 | 10048.993 | 67698.9936 | 77747.9866 | 0 | 0 | NORMAL
0.0056508 | 294.2611 | 0.0074924 | 297.0389 | 3 | 17181.4566 | 101548.4904 | 118729.9469 | 0 | 0 | NORMAL
0.0056508 | 294.2611 | 0.0074924 | 297.0389 | 4 | 26677.2973 | 135397.9871 | 162075.2844 | 0 | 0 | NORMAL
0.0056508 | 294.2611 | 0.0074924 | 308.15 | 1 | 5978.9828 | 30530.3443 | 36509.3272 | 0 | 0 | NORMAL
0.0056508 | 294.2611 | 0.0074924 | 308.15 | 2 | 11379.5112 | 61060.6887 | 72440.1999 | 0 | 0 | NORMAL
0.0056508 | 294.2611 | 0.0074924 | 308.15 | 3 | 19456.3354 | 91591.033 | 111047.3684 | 0 | 0 | NORMAL
0.0056508 | 294.2611 | 0.0074924 | 308.15 | 4 | 30209.4552 | 122121.3774 | 152330.8326 | 0 | 0 | NORMAL
0.0056508 | 294.2611 | 0.0074924 | 319.2611 | 1 | 6681.828 | 25778.3998 | 32460.2278 | 0 | 0 | NORMAL
0.0056508 | 294.2611 | 0.0074924 | 319.2611 | 2 | 12717.2028 | 51556.7996 | 64274.0024 | 0 | 0 | NORMAL
0.0056508 | 294.2611 | 0.0074924 | 319.2611 | 3 | 21743.479 | 77335.1994 | 99078.6784 | 0 | 0 | NORMAL
0.0056508 | 294.2611 | 0.0074924 | 319.2611 | 4 | 33760.6564 | 103113.5992 | 136874.2556 | 0 | 0 | NORMAL
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on J3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).
Note on K3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation