## RS0001
RS0001: Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 3.0.0 |  | ✓
| description | ASHRAE 90.1-2022 Appendix J curve set 'N': 75.0-150.0 ton, 4.69 COP, 7.18 IPLV liquid-cooled, positive displacement compressor chiller |  | ✓
| id | 9a343675-8185-47a3-9d68-4bf5e6cc31f8 |  | ✓
| data_timestamp | 2025-02-18T13:40Z |  | ✓
| data_version | 3 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2022 Appendix J curve set 'N' for Energy Cost Budget (ECB) Path B
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | SCROLL
performance |  |  |  | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| cycling_degradation_coefficient | 0 | - | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
performance.performance_map_evaporator_liquid_pressure_differential |  | $performance_map_evaporator_liqu |  | ✓
| condenser_type | LIQUID |  | ✓
performance.condenser_liquid_type
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| condenser_fouling_factor | 0 | m2-K/W
performance.performance_map_condenser_liquid_pressure_differential |  | $performance_map_condenser_liqui
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
performance.scaling
| minimum | 0.66667 | -
| maximum | 1.3333 | -
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on B20: Type of compressor speed control
Note on B21: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A22: Type of liquid in evaporator
Note on A23: An array of all liquid components within the liquid mixture
Note on B24: Defines whether concentration is defined on a volume or mass basis
Note on B25: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on A26: Data group describing the liquid pressure differential through the evaporator
Note on B27: Heat rejection method of the condenser
Note on A28: Type of liquid in condenser
Note on A29: An array of all liquid components within the liquid mixture
Note on B30: Defines whether concentration is defined on a volume or mass basis
Note on B31: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on A32: Data group describing the liquid pressure differential through the condenser
Note on A33: Data group describing cooling performance over a range of conditions
Note on A34: Data group describing standby performance
Note on A35: Specifies the range the performance data can be scaled to represent different capacity equipment
Note on B36: Minimum scaling factor
Note on B37: Maximum scaling factor

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_evaporator_liqu
performance.performance_map_evaporator_liquid_pressure_differential
grid_variables |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | evaporator_liquid_differential_pressure
m3/s | K | Pa
0.016952 | 275.3722 | 15000
0.016952 | 281.6685 | 15000
0.016952 | 287.9648 | 15000
0.016952 | 294.2611 | 15000
Note on A2: Data group defining the grid variables for the evaporator liquid pressure differential
Note on C2: Data group defining the lookup variables for the evaporator liquid pressure differential
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Pressure difference across the evaporator

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_condenser_liqui
performance.performance_map_condenser_liquid_pressure_differential
grid_variables |  | lookup_variables
condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | condenser_liquid_differential_pressure
m3/s | K | Pa
0.02232 | 285.9278 | 15000
0.02232 | 297.0389 | 15000
0.02232 | 308.15 | 15000
0.02232 | 319.2611 | 15000
Note on A2: Data group defining the grid variables for the condenser liquid pressure differential
Note on C2: Data group defining the lookup variables for the condenser liquid pressure differential
Note on A3: Condenser liquid flow
Note on B3: Entering condenser liquid temperature
Note on C3: Pressure difference across the condenser

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | oil_cooler_heat | auxiliary_heat | operation_state
m3/s | K | m3/s | K | - | W | W | W | W | W | -
0.016952 | 275.3722 | 0.02232 | 285.9278 | 1 | 14448.0701 | 92855.5518 | 107303.6219 | 0 | 0 | NORMAL
0.016952 | 275.3722 | 0.02232 | 285.9278 | 2 | 23986.9627 | 185711.1037 | 209698.0664 | 0 | 0 | NORMAL
0.016952 | 275.3722 | 0.02232 | 285.9278 | 3 | 40357.9885 | 278566.6555 | 318924.644 | 0 | 0 | NORMAL
0.016952 | 275.3722 | 0.02232 | 285.9278 | 4 | 63561.1475 | 371422.2073 | 434983.3548 | 0 | 0 | NORMAL
0.016952 | 275.3722 | 0.02232 | 297.0389 | 1 | 16605.2542 | 86584.6848 | 103189.939 | 0 | 0 | NORMAL
0.016952 | 275.3722 | 0.02232 | 297.0389 | 2 | 27568.3611 | 173169.3697 | 200737.7307 | 0 | 0 | NORMAL
0.016952 | 275.3722 | 0.02232 | 297.0389 | 3 | 46383.6798 | 259754.0545 | 306137.7344 | 0 | 0 | NORMAL
0.016952 | 275.3722 | 0.02232 | 297.0389 | 4 | 73051.2105 | 346338.7394 | 419389.9499 | 0 | 0 | NORMAL
0.016952 | 275.3722 | 0.02232 | 308.15 | 1 | 19182.4037 | 76577.1612 | 95759.5648 | 0 | 0 | NORMAL
0.016952 | 275.3722 | 0.02232 | 308.15 | 2 | 31846.994 | 153154.3224 | 185001.3164 | 0 | 0 | NORMAL
0.016952 | 275.3722 | 0.02232 | 308.15 | 3 | 53582.4662 | 229731.4836 | 283313.9498 | 0 | 0 | NORMAL
0.016952 | 275.3722 | 0.02232 | 308.15 | 4 | 84388.8202 | 306308.6447 | 390697.465 | 0 | 0 | NORMAL
0.016952 | 275.3722 | 0.02232 | 319.2611 | 1 | 20844.7724 | 62832.9809 | 83677.7533 | 0 | 0 | NORMAL
0.016952 | 275.3722 | 0.02232 | 319.2611 | 2 | 34606.8905 | 125665.9617 | 160272.8522 | 0 | 0 | NORMAL
0.016952 | 275.3722 | 0.02232 | 319.2611 | 3 | 58225.9832 | 188498.9426 | 246724.9258 | 0 | 0 | NORMAL
0.016952 | 275.3722 | 0.02232 | 319.2611 | 4 | 91702.0507 | 251331.9235 | 343033.9741 | 0 | 0 | NORMAL
0.016952 | 281.6685 | 0.02232 | 285.9278 | 1 | 14948.3864 | 114043.8713 | 128992.2577 | 0 | 0 | NORMAL
0.016952 | 281.6685 | 0.02232 | 285.9278 | 2 | 24817.5975 | 228087.7427 | 252905.3402 | 0 | 0 | NORMAL
0.016952 | 281.6685 | 0.02232 | 285.9278 | 3 | 41755.5289 | 342131.614 | 383887.1429 | 0 | 0 | NORMAL
0.016952 | 281.6685 | 0.02232 | 285.9278 | 4 | 65762.1806 | 456175.4854 | 521937.6659 | 0 | 0 | NORMAL
0.016952 | 281.6685 | 0.02232 | 297.0389 | 1 | 17472.7832 | 107932.1582 | 125404.9415 | 0 | 0 | NORMAL
0.016952 | 281.6685 | 0.02232 | 297.0389 | 2 | 29008.6495 | 215864.3165 | 244872.966 | 0 | 0 | NORMAL
0.016952 | 281.6685 | 0.02232 | 297.0389 | 3 | 48806.9605 | 323796.4747 | 372603.4352 | 0 | 0 | NORMAL
0.016952 | 281.6685 | 0.02232 | 297.0389 | 4 | 76867.7164 | 431728.633 | 508596.3493 | 0 | 0 | NORMAL
0.016952 | 281.6685 | 0.02232 | 308.15 | 1 | 21110.7374 | 98083.7885 | 119194.5259 | 0 | 0 | NORMAL
0.016952 | 281.6685 | 0.02232 | 308.15 | 2 | 35048.4506 | 196167.577 | 231216.0276 | 0 | 0 | NORMAL
0.016952 | 281.6685 | 0.02232 | 308.15 | 3 | 58968.9067 | 294251.3655 | 353220.2722 | 0 | 0 | NORMAL
0.016952 | 281.6685 | 0.02232 | 308.15 | 4 | 92872.1057 | 392335.1539 | 485207.2596 | 0 | 0 | NORMAL
0.016952 | 281.6685 | 0.02232 | 319.2611 | 1 | 24598.4847 | 84498.7621 | 109097.2467 | 0 | 0 | NORMAL
0.016952 | 281.6685 | 0.02232 | 319.2611 | 2 | 40838.8755 | 168997.5241 | 209836.3996 | 0 | 0 | NORMAL
0.016952 | 281.6685 | 0.02232 | 319.2611 | 3 | 68711.2782 | 253496.2862 | 322207.5643 | 0 | 0 | NORMAL
0.016952 | 281.6685 | 0.02232 | 319.2611 | 4 | 108215.6927 | 337995.0482 | 446210.741 | 0 | 0 | NORMAL
0.016952 | 287.9648 | 0.02232 | 285.9278 | 1 | 15428.8014 | 118943.597 | 134372.3984 | 0 | 0 | NORMAL
0.016952 | 287.9648 | 0.02232 | 285.9278 | 2 | 25615.1916 | 237887.194 | 263502.3856 | 0 | 0 | NORMAL
0.016952 | 287.9648 | 0.02232 | 285.9278 | 3 | 43097.4784 | 356830.791 | 399928.2694 | 0 | 0 | NORMAL
0.016952 | 287.9648 | 0.02232 | 285.9278 | 4 | 67875.6619 | 475774.388 | 543650.0499 | 0 | 0 | NORMAL
0.016952 | 287.9648 | 0.02232 | 297.0389 | 1 | 17531.0089 | 112991.0378 | 130522.0467 | 0 | 0 | NORMAL
0.016952 | 287.9648 | 0.02232 | 297.0389 | 2 | 29105.3167 | 225982.0756 | 255087.3923 | 0 | 0 | NORMAL
0.016952 | 287.9648 | 0.02232 | 297.0389 | 3 | 48969.6029 | 338973.1134 | 387942.7163 | 0 | 0 | NORMAL
0.016952 | 287.9648 | 0.02232 | 297.0389 | 4 | 77123.8673 | 451964.1512 | 529088.0185 | 0 | 0 | NORMAL
0.016952 | 287.9648 | 0.02232 | 308.15 | 1 | 20983.3538 | 103301.8219 | 124285.1757 | 0 | 0 | NORMAL
0.016952 | 287.9648 | 0.02232 | 308.15 | 2 | 34836.9659 | 206603.6439 | 241440.6098 | 0 | 0 | NORMAL
0.016952 | 287.9648 | 0.02232 | 308.15 | 3 | 58613.0844 | 309905.4658 | 368518.5502 | 0 | 0 | NORMAL
0.016952 | 287.9648 | 0.02232 | 308.15 | 4 | 92311.7093 | 413207.2877 | 505518.997 | 0 | 0 | NORMAL
0.016952 | 287.9648 | 0.02232 | 319.2611 | 1 | 24593.0541 | 89875.9494 | 114469.0035 | 0 | 0 | NORMAL
0.016952 | 287.9648 | 0.02232 | 319.2611 | 2 | 40829.8595 | 179751.8988 | 220581.7583 | 0 | 0 | NORMAL
0.016952 | 287.9648 | 0.02232 | 319.2611 | 3 | 68696.1089 | 269627.8482 | 338323.9571 | 0 | 0 | NORMAL
0.016952 | 287.9648 | 0.02232 | 319.2611 | 4 | 108191.8021 | 359503.7976 | 467695.5997 | 0 | 0 | NORMAL
0.016952 | 294.2611 | 0.02232 | 285.9278 | 1 | 16296.244 | 107554.7288 | 123850.9728 | 0 | 0 | NORMAL
0.016952 | 294.2611 | 0.02232 | 285.9278 | 2 | 27055.3364 | 215109.4576 | 242164.794 | 0 | 0 | NORMAL
0.016952 | 294.2611 | 0.02232 | 285.9278 | 3 | 45520.5175 | 322664.1864 | 368184.7039 | 0 | 0 | NORMAL
0.016952 | 294.2611 | 0.02232 | 285.9278 | 4 | 71691.7873 | 430218.9151 | 501910.7024 | 0 | 0 | NORMAL
0.016952 | 294.2611 | 0.02232 | 297.0389 | 1 | 17460.4385 | 101761.3235 | 119221.762 | 0 | 0 | NORMAL
0.016952 | 294.2611 | 0.02232 | 297.0389 | 2 | 28988.1545 | 203522.647 | 232510.8014 | 0 | 0 | NORMAL
0.016952 | 294.2611 | 0.02232 | 297.0389 | 3 | 48772.4777 | 305283.9705 | 354056.4482 | 0 | 0 | NORMAL
0.016952 | 294.2611 | 0.02232 | 297.0389 | 4 | 76813.4083 | 407045.2939 | 483858.7022 | 0 | 0 | NORMAL
0.016952 | 294.2611 | 0.02232 | 308.15 | 1 | 19754.3389 | 92231.2615 | 111985.6004 | 0 | 0 | NORMAL
0.016952 | 294.2611 | 0.02232 | 308.15 | 2 | 32796.5318 | 184462.523 | 217259.0548 | 0 | 0 | NORMAL
0.016952 | 294.2611 | 0.02232 | 308.15 | 3 | 55180.0605 | 276693.7845 | 331873.8451 | 0 | 0 | NORMAL
0.016952 | 294.2611 | 0.02232 | 308.15 | 4 | 86904.925 | 368925.0461 | 455829.971 | 0 | 0 | NORMAL
0.016952 | 294.2611 | 0.02232 | 319.2611 | 1 | 22056.1451 | 78964.5429 | 101020.688 | 0 | 0 | NORMAL
0.016952 | 294.2611 | 0.02232 | 319.2611 | 2 | 36618.0346 | 157929.0858 | 194547.1204 | 0 | 0 | NORMAL
0.016952 | 294.2611 | 0.02232 | 319.2611 | 3 | 61609.7268 | 236893.6286 | 298503.3555 | 0 | 0 | NORMAL
0.016952 | 294.2611 | 0.02232 | 319.2611 | 4 | 97031.2218 | 315858.1715 | 412889.3933 | 0 | 0 | NORMAL
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on J3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).
Note on K3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation