## RS0001
RS0001: Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 3.0.0 |  | ✓
| description | ASHRAE 90.1-2022 Appendix J curve set 'O': 150.0-300.0 ton, 5.17 COP, 7.99 IPLV liquid-cooled, positive displacement compressor chiller |  | ✓
| id | 452f9c50-78b6-4a45-8b74-f126746b4772 |  | ✓
| data_timestamp | 2025-02-18T13:40Z |  | ✓
| data_version | 3 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2022 Appendix J curve set 'O' for Energy Cost Budget (ECB) Path B
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | SCROLL
performance |  |  |  | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| cycling_degradation_coefficient | 0 | - | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
performance.performance_map_evaporator_liquid_pressure_differential |  | $performance_map_evaporator_liqu |  | ✓
| condenser_type | LIQUID |  | ✓
performance.condenser_liquid_type
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| condenser_fouling_factor | 0 | m2-K/W
performance.performance_map_condenser_liquid_pressure_differential |  | $performance_map_condenser_liqui
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
performance.scaling
| minimum | 0.66667 | -
| maximum | 1.3333 | -
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on B20: Type of compressor speed control
Note on B21: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A22: Type of liquid in evaporator
Note on A23: An array of all liquid components within the liquid mixture
Note on B24: Defines whether concentration is defined on a volume or mass basis
Note on B25: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on A26: Data group describing the liquid pressure differential through the evaporator
Note on B27: Heat rejection method of the condenser
Note on A28: Type of liquid in condenser
Note on A29: An array of all liquid components within the liquid mixture
Note on B30: Defines whether concentration is defined on a volume or mass basis
Note on B31: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on A32: Data group describing the liquid pressure differential through the condenser
Note on A33: Data group describing cooling performance over a range of conditions
Note on A34: Data group describing standby performance
Note on A35: Specifies the range the performance data can be scaled to represent different capacity equipment
Note on B36: Minimum scaling factor
Note on B37: Maximum scaling factor

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_evaporator_liqu
performance.performance_map_evaporator_liquid_pressure_differential
grid_variables |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | evaporator_liquid_differential_pressure
m3/s | K | Pa
0.033905 | 275.3722 | 15000
0.033905 | 281.6685 | 15000
0.033905 | 287.9648 | 15000
0.033905 | 294.2611 | 15000
Note on A2: Data group defining the grid variables for the evaporator liquid pressure differential
Note on C2: Data group defining the lookup variables for the evaporator liquid pressure differential
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Pressure difference across the evaporator

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_condenser_liqui
performance.performance_map_condenser_liquid_pressure_differential
grid_variables |  | lookup_variables
condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | condenser_liquid_differential_pressure
m3/s | K | Pa
0.043908 | 285.9278 | 15000
0.043908 | 297.0389 | 15000
0.043908 | 308.15 | 15000
0.043908 | 319.2611 | 15000
Note on A2: Data group defining the grid variables for the condenser liquid pressure differential
Note on C2: Data group defining the lookup variables for the condenser liquid pressure differential
Note on A3: Condenser liquid flow
Note on B3: Entering condenser liquid temperature
Note on C3: Pressure difference across the condenser

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | oil_cooler_heat | auxiliary_heat | operation_state
m3/s | K | m3/s | K | - | W | W | W | W | W | -
0.033905 | 275.3722 | 0.043908 | 285.9278 | 1 | 20324.5561 | 183373.7614 | 203698.3175 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043908 | 285.9278 | 2 | 40230.0376 | 366747.5228 | 406977.5604 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043908 | 285.9278 | 3 | 69630.004 | 550121.2842 | 619751.2883 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043908 | 285.9278 | 4 | 108524.4554 | 733495.0456 | 842019.501 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043908 | 297.0389 | 1 | 25123.0842 | 177920.6849 | 203043.7691 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043908 | 297.0389 | 2 | 49728.1524 | 355841.3699 | 405569.5223 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043908 | 297.0389 | 3 | 86069.3069 | 533762.0548 | 619831.3617 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043908 | 297.0389 | 4 | 134146.5477 | 711682.7398 | 845829.2874 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043908 | 308.15 | 1 | 29014.8168 | 163284.7136 | 192299.5305 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043908 | 308.15 | 2 | 57431.3735 | 326569.4273 | 384000.8008 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043908 | 308.15 | 3 | 99402.0142 | 489854.1409 | 589256.1551 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043908 | 308.15 | 4 | 154926.7388 | 653138.8546 | 808065.5934 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043908 | 319.2611 | 1 | 30725.6009 | 139465.8475 | 170191.4484 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043908 | 319.2611 | 2 | 60817.6668 | 278931.6951 | 339749.3618 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043908 | 319.2611 | 3 | 105262.9983 | 418397.5426 | 523660.541 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043908 | 319.2611 | 4 | 164061.5956 | 557863.3902 | 721924.9858 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043908 | 285.9278 | 1 | 21102.4763 | 213276.0565 | 234378.5329 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043908 | 285.9278 | 2 | 41769.8381 | 426552.1131 | 468321.9512 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043908 | 285.9278 | 3 | 72295.0852 | 639828.1696 | 712123.2548 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043908 | 285.9278 | 4 | 112678.2176 | 853104.2261 | 965782.4438 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043908 | 297.0389 | 1 | 26237.015 | 210092.653 | 236329.668 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043908 | 297.0389 | 2 | 51933.0458 | 420185.306 | 472118.3518 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043908 | 297.0389 | 3 | 89885.5284 | 630277.959 | 720163.4874 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043908 | 297.0389 | 4 | 140094.4628 | 840370.612 | 980465.0748 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043908 | 308.15 | 1 | 31032.2484 | 197726.3546 | 228758.603 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043908 | 308.15 | 2 | 61424.639 | 395452.7093 | 456877.3483 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043908 | 308.15 | 3 | 106313.5437 | 593179.0639 | 699492.6076 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043908 | 308.15 | 4 | 165698.9625 | 790905.4186 | 956604.3811 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043908 | 319.2611 | 1 | 34377.7172 | 176177.1615 | 210554.8787 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043908 | 319.2611 | 2 | 68046.596 | 352354.323 | 420400.9189 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043908 | 319.2611 | 3 | 117774.8029 | 528531.4844 | 646306.2874 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043908 | 319.2611 | 4 | 183562.3381 | 704708.6459 | 888270.984 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043908 | 285.9278 | 1 | 21933.025 | 218270.9977 | 240204.0227 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043908 | 285.9278 | 2 | 43413.8103 | 436541.9955 | 479955.8057 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043908 | 285.9278 | 3 | 75140.4663 | 654812.9932 | 729953.4595 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043908 | 285.9278 | 4 | 117112.993 | 873083.9909 | 990196.984 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043908 | 297.0389 | 1 | 26516.6115 | 217357.2671 | 243873.8786 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043908 | 297.0389 | 2 | 52486.4737 | 434714.5343 | 487201.008 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043908 | 297.0389 | 3 | 90843.3995 | 652071.8014 | 742915.2009 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043908 | 297.0389 | 4 | 141587.3887 | 869429.0685 | 1011016.4573 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043908 | 308.15 | 1 | 31012.2971 | 207260.6417 | 238272.9388 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043908 | 308.15 | 2 | 61385.1478 | 414521.2834 | 475906.4313 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043908 | 308.15 | 3 | 106245.1925 | 621781.9252 | 728027.1177 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043908 | 308.15 | 4 | 165592.4312 | 829042.5669 | 994634.998 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043908 | 319.2611 | 1 | 34473.3163 | 187981.1215 | 222454.4378 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043908 | 319.2611 | 2 | 68235.823 | 375962.243 | 444198.066 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043908 | 319.2611 | 3 | 118102.3165 | 563943.3645 | 682045.681 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043908 | 319.2611 | 4 | 184072.7966 | 751924.486 | 935997.2826 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043908 | 285.9278 | 1 | 22902.3596 | 198358.585 | 221260.9446 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043908 | 285.9278 | 2 | 45332.4925 | 396717.17 | 442049.6626 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043908 | 285.9278 | 3 | 78461.3146 | 595075.755 | 673537.0697 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043908 | 285.9278 | 4 | 122288.8258 | 793434.3401 | 915723.1659 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043908 | 297.0389 | 1 | 26470.3991 | 199714.5274 | 226184.9265 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043908 | 297.0389 | 2 | 52395.0018 | 399429.0547 | 451824.0565 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043908 | 297.0389 | 3 | 90685.0802 | 599143.5821 | 689828.6623 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043908 | 297.0389 | 4 | 141340.6343 | 798858.1094 | 940198.7437 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043908 | 308.15 | 1 | 29885.8564 | 191887.5749 | 221773.4313 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043908 | 308.15 | 2 | 59155.4926 | 383775.1498 | 442930.6423 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043908 | 308.15 | 3 | 102386.1133 | 575662.7246 | 678048.8379 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043908 | 308.15 | 4 | 159577.7184 | 767550.2995 | 927128.0179 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043908 | 319.2611 | 1 | 32365.6596 | 174877.7276 | 207243.3872 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043908 | 319.2611 | 2 | 64063.9677 | 349755.4552 | 413819.4229 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043908 | 319.2611 | 3 | 110881.6842 | 524633.1828 | 635514.867 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043908 | 319.2611 | 4 | 172818.8093 | 699510.9104 | 872329.7197 | 0 | 0 | NORMAL
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on J3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).
Note on K3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation