## RS0001
RS0001: Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 3.0.0 |  | ✓
| description | ASHRAE 90.1-2022 Appendix J curve set 'P': 300.0-600.0 ton, 5.63 COP, 8.58 IPLV liquid-cooled, positive displacement compressor chiller |  | ✓
| id | 1ab8975a-a3bd-4156-8c98-fdd4369a27f0 |  | ✓
| data_timestamp | 2025-02-18T13:40Z |  | ✓
| data_version | 3 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2022 Appendix J curve set 'P' for Energy Cost Budget (ECB) Path B
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | SCROLL
performance |  |  |  | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| cycling_degradation_coefficient | 0 | - | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
performance.performance_map_evaporator_liquid_pressure_differential |  | $performance_map_evaporator_liqu |  | ✓
| condenser_type | LIQUID |  | ✓
performance.condenser_liquid_type
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| condenser_fouling_factor | 0 | m2-K/W
performance.performance_map_condenser_liquid_pressure_differential |  | $performance_map_condenser_liqui
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
performance.scaling
| minimum | 0.66667 | -
| maximum | 1.3333 | -
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on B20: Type of compressor speed control
Note on B21: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A22: Type of liquid in evaporator
Note on A23: An array of all liquid components within the liquid mixture
Note on B24: Defines whether concentration is defined on a volume or mass basis
Note on B25: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on A26: Data group describing the liquid pressure differential through the evaporator
Note on B27: Heat rejection method of the condenser
Note on A28: Type of liquid in condenser
Note on A29: An array of all liquid components within the liquid mixture
Note on B30: Defines whether concentration is defined on a volume or mass basis
Note on B31: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on A32: Data group describing the liquid pressure differential through the condenser
Note on A33: Data group describing cooling performance over a range of conditions
Note on A34: Data group describing standby performance
Note on A35: Specifies the range the performance data can be scaled to represent different capacity equipment
Note on B36: Minimum scaling factor
Note on B37: Maximum scaling factor

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_evaporator_liqu
performance.performance_map_evaporator_liquid_pressure_differential
grid_variables |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | evaporator_liquid_differential_pressure
m3/s | K | Pa
0.067809 | 275.3722 | 15000
0.067809 | 281.6685 | 15000
0.067809 | 287.9648 | 15000
0.067809 | 294.2611 | 15000
Note on A2: Data group defining the grid variables for the evaporator liquid pressure differential
Note on C2: Data group defining the lookup variables for the evaporator liquid pressure differential
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Pressure difference across the evaporator

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_condenser_liqui
performance.performance_map_condenser_liquid_pressure_differential
grid_variables |  | lookup_variables
condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | condenser_liquid_differential_pressure
m3/s | K | Pa
0.086666 | 285.9278 | 15000
0.086666 | 297.0389 | 15000
0.086666 | 308.15 | 15000
0.086666 | 319.2611 | 15000
Note on A2: Data group defining the grid variables for the condenser liquid pressure differential
Note on C2: Data group defining the lookup variables for the condenser liquid pressure differential
Note on A3: Condenser liquid flow
Note on B3: Entering condenser liquid temperature
Note on C3: Pressure difference across the condenser

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | oil_cooler_heat | auxiliary_heat | operation_state
m3/s | K | m3/s | K | - | W | W | W | W | W | -
0.067809 | 275.3722 | 0.086666 | 285.9278 | 1 | 40821.7998 | 377205.1988 | 418026.9987 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.086666 | 285.9278 | 2 | 79342.4376 | 754410.3976 | 833752.8353 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.086666 | 285.9278 | 3 | 138164.4471 | 1131615.5965 | 1269780.0436 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.086666 | 285.9278 | 4 | 217287.8283 | 1508820.7953 | 1726108.6236 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.086666 | 297.0389 | 1 | 49242.829 | 365566.8565 | 414809.6855 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.086666 | 297.0389 | 2 | 95709.7948 | 731133.7131 | 826843.5079 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.086666 | 297.0389 | 3 | 166666.0526 | 1096700.5696 | 1263366.6223 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.086666 | 297.0389 | 4 | 262111.6024 | 1462267.4262 | 1724379.0286 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.086666 | 308.15 | 1 | 54927.7002 | 336930.3898 | 391858.0901 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.086666 | 308.15 | 2 | 106759.0759 | 673860.7797 | 780619.8556 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.086666 | 308.15 | 3 | 185906.9262 | 1010791.1695 | 1196698.0957 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.086666 | 308.15 | 4 | 292371.2512 | 1347721.5593 | 1640092.8105 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.086666 | 319.2611 | 1 | 56274.0926 | 291295.7987 | 347569.8913 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.086666 | 319.2611 | 2 | 109375.9633 | 582591.5973 | 691967.5606 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.086666 | 319.2611 | 3 | 190463.8923 | 873887.396 | 1064351.2883 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.086666 | 319.2611 | 4 | 299537.8797 | 1165183.1947 | 1464721.0744 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.086666 | 285.9278 | 1 | 39305.8708 | 421687.1901 | 460993.0609 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.086666 | 285.9278 | 2 | 76396.0338 | 843374.3803 | 919770.4141 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.086666 | 285.9278 | 3 | 133033.6714 | 1265061.5704 | 1398095.2418 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.086666 | 285.9278 | 4 | 209218.7835 | 1686748.7606 | 1895967.5441 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.086666 | 297.0389 | 1 | 48498.6715 | 416470.3616 | 464969.033 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.086666 | 297.0389 | 2 | 94263.4286 | 832940.7231 | 927204.1517 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.086666 | 297.0389 | 3 | 164147.3957 | 1249411.0847 | 1413558.4803 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.086666 | 297.0389 | 4 | 258150.5725 | 1665881.4462 | 1924032.0187 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.086666 | 308.15 | 1 | 55800.0218 | 394255.4085 | 450055.4303 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.086666 | 308.15 | 2 | 108454.5454 | 788510.817 | 896965.3625 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.086666 | 308.15 | 3 | 188859.364 | 1182766.2255 | 1371625.5895 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.086666 | 308.15 | 4 | 297014.4774 | 1577021.6341 | 1874036.1115 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.086666 | 319.2611 | 1 | 59808.2862 | 355042.331 | 414850.6172 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.086666 | 319.2611 | 2 | 116245.1247 | 710084.6621 | 826329.7867 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.086666 | 319.2611 | 3 | 202425.6358 | 1065126.9931 | 1267552.6289 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.086666 | 319.2611 | 4 | 318349.8195 | 1420169.3241 | 1738519.1436 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.086666 | 285.9278 | 1 | 39418.6809 | 426737.766 | 466156.4469 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.086666 | 285.9278 | 2 | 76615.2948 | 853475.532 | 930090.8268 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.086666 | 285.9278 | 3 | 133415.4857 | 1280213.298 | 1413628.7837 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.086666 | 285.9278 | 4 | 209819.2534 | 1706951.0641 | 1916770.3175 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.086666 | 297.0389 | 1 | 48089.0173 | 427942.4511 | 476031.4684 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.086666 | 297.0389 | 2 | 93467.2129 | 855884.9022 | 949352.1151 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.086666 | 297.0389 | 3 | 162760.8905 | 1283827.3533 | 1446588.2437 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.086666 | 297.0389 | 4 | 255970.0499 | 1711769.8044 | 1967739.8543 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.086666 | 308.15 | 1 | 55315.9208 | 412149.0117 | 467464.9326 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.086666 | 308.15 | 2 | 107513.6328 | 824298.0235 | 931811.6562 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.086666 | 308.15 | 3 | 187220.888 | 1236447.0352 | 1423667.9232 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.086666 | 308.15 | 4 | 294437.6866 | 1648596.047 | 1943033.7335 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.086666 | 319.2611 | 1 | 59898.4413 | 379357.4479 | 439255.8892 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.086666 | 319.2611 | 2 | 116420.3528 | 758714.8959 | 875135.2487 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.086666 | 319.2611 | 3 | 202730.7726 | 1138072.3438 | 1340803.1164 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.086666 | 319.2611 | 4 | 318829.7006 | 1517429.7917 | 1836259.4924 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.086666 | 285.9278 | 1 | 41474.1878 | 392356.9264 | 433831.1143 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.086666 | 285.9278 | 2 | 80610.4379 | 784713.8528 | 865324.2907 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.086666 | 285.9278 | 3 | 140372.5033 | 1177070.7793 | 1317443.2825 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.086666 | 285.9278 | 4 | 220760.3839 | 1569427.7057 | 1790188.0896 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.086666 | 297.0389 | 1 | 48984.1398 | 399983.1252 | 448967.265 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.086666 | 297.0389 | 2 | 95206.999 | 799966.2504 | 895173.2494 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.086666 | 297.0389 | 3 | 165790.4997 | 1199949.3755 | 1365739.8753 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.086666 | 297.0389 | 4 | 260734.6419 | 1599932.5007 | 1860667.1426 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.086666 | 308.15 | 1 | 55101.9862 | 390611.1995 | 445713.1857 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.086666 | 308.15 | 2 | 107097.8232 | 781222.399 | 888320.2222 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.086666 | 308.15 | 3 | 186496.8102 | 1171833.5985 | 1358330.4087 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.086666 | 308.15 | 4 | 293298.9472 | 1562444.798 | 1855743.7452 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.086666 | 319.2611 | 1 | 58827.4623 | 364241.1494 | 423068.6117 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.086666 | 319.2611 | 2 | 114338.767 | 728482.2987 | 842821.0657 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.086666 | 319.2611 | 3 | 199105.9639 | 1092723.4481 | 1291829.4121 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.086666 | 319.2611 | 4 | 313129.0532 | 1456964.5975 | 1770093.6507 | 0 | 0 | NORMAL
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on J3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).
Note on K3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation