## RS0001
RS0001: Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 3.0.0 |  | ✓
| description | ASHRAE 90.1-2022 Appendix J curve set 'Q': 600.0+ ton, 6.01 COP, 9.25 IPLV liquid-cooled, positive displacement compressor chiller |  | ✓
| id | 757aa44b-2f8b-421a-ae10-a7245c2883db |  | ✓
| data_timestamp | 2025-02-18T13:40Z |  | ✓
| data_version | 3 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2022 Appendix J curve set 'Q' for Energy Cost Budget (ECB) Path B
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | SCROLL
performance |  |  |  | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| cycling_degradation_coefficient | 0 | - | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
performance.performance_map_evaporator_liquid_pressure_differential |  | $performance_map_evaporator_liqu |  | ✓
| condenser_type | LIQUID |  | ✓
performance.condenser_liquid_type
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| condenser_fouling_factor | 0 | m2-K/W
performance.performance_map_condenser_liquid_pressure_differential |  | $performance_map_condenser_liqui
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
performance.scaling
| minimum | 0.92308 | -
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on B20: Type of compressor speed control
Note on B21: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A22: Type of liquid in evaporator
Note on A23: An array of all liquid components within the liquid mixture
Note on B24: Defines whether concentration is defined on a volume or mass basis
Note on B25: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on A26: Data group describing the liquid pressure differential through the evaporator
Note on B27: Heat rejection method of the condenser
Note on A28: Type of liquid in condenser
Note on A29: An array of all liquid components within the liquid mixture
Note on B30: Defines whether concentration is defined on a volume or mass basis
Note on B31: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on A32: Data group describing the liquid pressure differential through the condenser
Note on A33: Data group describing cooling performance over a range of conditions
Note on A34: Data group describing standby performance
Note on A35: Specifies the range the performance data can be scaled to represent different capacity equipment
Note on B36: Minimum scaling factor

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_evaporator_liqu
performance.performance_map_evaporator_liquid_pressure_differential
grid_variables |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | evaporator_liquid_differential_pressure
m3/s | K | Pa
0.097947 | 275.3722 | 15000
0.097947 | 281.6685 | 15000
0.097947 | 287.9648 | 15000
0.097947 | 294.2611 | 15000
Note on A2: Data group defining the grid variables for the evaporator liquid pressure differential
Note on C2: Data group defining the lookup variables for the evaporator liquid pressure differential
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Pressure difference across the evaporator

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_condenser_liqui
performance.performance_map_condenser_liquid_pressure_differential
grid_variables |  | lookup_variables
condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | condenser_liquid_differential_pressure
m3/s | K | Pa
0.12398 | 285.9278 | 15000
0.12398 | 297.0389 | 15000
0.12398 | 308.15 | 15000
0.12398 | 319.2611 | 15000
Note on A2: Data group defining the grid variables for the condenser liquid pressure differential
Note on C2: Data group defining the lookup variables for the condenser liquid pressure differential
Note on A3: Condenser liquid flow
Note on B3: Entering condenser liquid temperature
Note on C3: Pressure difference across the condenser

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | oil_cooler_heat | auxiliary_heat | operation_state
m3/s | K | m3/s | K | - | W | W | W | W | W | -
0.097947 | 275.3722 | 0.12398 | 285.9278 | 1 | 48576.3778 | 539577.5368 | 588153.9146 | 0 | 0 | NORMAL
0.097947 | 275.3722 | 0.12398 | 285.9278 | 2 | 103723.6786 | 1079155.0736 | 1182878.7521 | 0 | 0 | NORMAL
0.097947 | 275.3722 | 0.12398 | 285.9278 | 3 | 183131.4951 | 1618732.6103 | 1801864.1054 | 0 | 0 | NORMAL
0.097947 | 275.3722 | 0.12398 | 285.9278 | 4 | 286799.8273 | 2158310.1471 | 2445109.9745 | 0 | 0 | NORMAL
0.097947 | 275.3722 | 0.12398 | 297.0389 | 1 | 62202.6798 | 539128.1068 | 601330.7866 | 0 | 0 | NORMAL
0.097947 | 275.3722 | 0.12398 | 297.0389 | 2 | 132819.5113 | 1078256.2136 | 1211075.7249 | 0 | 0 | NORMAL
0.097947 | 275.3722 | 0.12398 | 297.0389 | 3 | 234502.2468 | 1617384.3204 | 1851886.5672 | 0 | 0 | NORMAL
0.097947 | 275.3722 | 0.12398 | 297.0389 | 4 | 367250.8865 | 2156512.4272 | 2523763.3137 | 0 | 0 | NORMAL
0.097947 | 275.3722 | 0.12398 | 308.15 | 1 | 68274.0304 | 500297.2158 | 568571.2462 | 0 | 0 | NORMAL
0.097947 | 275.3722 | 0.12398 | 308.15 | 2 | 145783.4837 | 1000594.4315 | 1146377.9152 | 0 | 0 | NORMAL
0.097947 | 275.3722 | 0.12398 | 308.15 | 3 | 257391.0577 | 1500891.6473 | 1758282.705 | 0 | 0 | NORMAL
0.097947 | 275.3722 | 0.12398 | 308.15 | 4 | 403096.7523 | 2001188.863 | 2404285.6153 | 0 | 0 | NORMAL
0.097947 | 275.3722 | 0.12398 | 319.2611 | 1 | 64858.1476 | 423084.8636 | 487943.0113 | 0 | 0 | NORMAL
0.097947 | 275.3722 | 0.12398 | 319.2611 | 2 | 138489.6519 | 846169.7273 | 984659.3792 | 0 | 0 | NORMAL
0.097947 | 275.3722 | 0.12398 | 319.2611 | 3 | 244513.2815 | 1269254.5909 | 1513767.8724 | 0 | 0 | NORMAL
0.097947 | 275.3722 | 0.12398 | 319.2611 | 4 | 382929.0362 | 1692339.4546 | 2075268.4908 | 0 | 0 | NORMAL
0.097947 | 281.6685 | 0.12398 | 285.9278 | 1 | 44052.0788 | 577337.8312 | 621389.91 | 0 | 0 | NORMAL
0.097947 | 281.6685 | 0.12398 | 285.9278 | 2 | 94063.0789 | 1154675.6624 | 1248738.7413 | 0 | 0 | NORMAL
0.097947 | 281.6685 | 0.12398 | 285.9278 | 3 | 166075.0227 | 1732013.4937 | 1898088.5163 | 0 | 0 | NORMAL
0.097947 | 281.6685 | 0.12398 | 285.9278 | 4 | 260087.9101 | 2309351.3249 | 2569439.235 | 0 | 0 | NORMAL
0.097947 | 281.6685 | 0.12398 | 297.0389 | 1 | 58652.5171 | 591921.1402 | 650573.6573 | 0 | 0 | NORMAL
0.097947 | 281.6685 | 0.12398 | 297.0389 | 2 | 125238.9558 | 1183842.2803 | 1309081.2361 | 0 | 0 | NORMAL
0.097947 | 281.6685 | 0.12398 | 297.0389 | 3 | 221118.2396 | 1775763.4205 | 1996881.6601 | 0 | 0 | NORMAL
0.097947 | 281.6685 | 0.12398 | 297.0389 | 4 | 346290.3687 | 2367684.5607 | 2713974.9294 | 0 | 0 | NORMAL
0.097947 | 281.6685 | 0.12398 | 308.15 | 1 | 66820.0503 | 568122.988 | 634943.0383 | 0 | 0 | NORMAL
0.097947 | 281.6685 | 0.12398 | 308.15 | 2 | 142678.8437 | 1136245.9761 | 1278924.8198 | 0 | 0 | NORMAL
0.097947 | 281.6685 | 0.12398 | 308.15 | 3 | 251909.596 | 1704368.9641 | 1956278.5601 | 0 | 0 | NORMAL
0.097947 | 281.6685 | 0.12398 | 308.15 | 4 | 394512.3072 | 2272491.9521 | 2667004.2593 | 0 | 0 | NORMAL
0.097947 | 281.6685 | 0.12398 | 319.2611 | 1 | 66725.4769 | 505943.3748 | 572668.8517 | 0 | 0 | NORMAL
0.097947 | 281.6685 | 0.12398 | 319.2611 | 2 | 142476.9039 | 1011886.7497 | 1154363.6536 | 0 | 0 | NORMAL
0.097947 | 281.6685 | 0.12398 | 319.2611 | 3 | 251553.057 | 1517830.1245 | 1769383.1815 | 0 | 0 | NORMAL
0.097947 | 281.6685 | 0.12398 | 319.2611 | 4 | 393953.9361 | 2023773.4994 | 2417727.4355 | 0 | 0 | NORMAL
0.097947 | 287.9648 | 0.12398 | 285.9278 | 1 | 43093.0454 | 573049.1028 | 616142.1482 | 0 | 0 | NORMAL
0.097947 | 287.9648 | 0.12398 | 285.9278 | 2 | 92015.2838 | 1146098.2055 | 1238113.4893 | 0 | 0 | NORMAL
0.097947 | 287.9648 | 0.12398 | 285.9278 | 3 | 162459.4955 | 1719147.3083 | 1881606.8038 | 0 | 0 | NORMAL
0.097947 | 287.9648 | 0.12398 | 285.9278 | 4 | 254425.6806 | 2292196.411 | 2546622.0916 | 0 | 0 | NORMAL
0.097947 | 287.9648 | 0.12398 | 297.0389 | 1 | 57507.7845 | 602665.1506 | 660172.9351 | 0 | 0 | NORMAL
0.097947 | 287.9648 | 0.12398 | 297.0389 | 2 | 122794.6426 | 1205330.3012 | 1328124.9438 | 0 | 0 | NORMAL
0.097947 | 287.9648 | 0.12398 | 297.0389 | 3 | 216802.6317 | 1807995.4518 | 2024798.0835 | 0 | 0 | NORMAL
0.097947 | 287.9648 | 0.12398 | 297.0389 | 4 | 339531.7518 | 2410660.6025 | 2750192.3543 | 0 | 0 | NORMAL
0.097947 | 287.9648 | 0.12398 | 308.15 | 1 | 66152.1655 | 593899.7374 | 660051.9029 | 0 | 0 | NORMAL
0.097947 | 287.9648 | 0.12398 | 308.15 | 2 | 141252.7294 | 1187799.4748 | 1329052.2042 | 0 | 0 | NORMAL
0.097947 | 287.9648 | 0.12398 | 308.15 | 3 | 249391.6902 | 1781699.2122 | 2031090.9025 | 0 | 0 | NORMAL
0.097947 | 287.9648 | 0.12398 | 308.15 | 4 | 390569.0481 | 2375598.9496 | 2766167.9977 | 0 | 0 | NORMAL
0.097947 | 287.9648 | 0.12398 | 319.2611 | 1 | 67300.0678 | 546752.8631 | 614052.931 | 0 | 0 | NORMAL
0.097947 | 287.9648 | 0.12398 | 319.2611 | 2 | 143703.8107 | 1093505.7263 | 1237209.537 | 0 | 0 | NORMAL
0.097947 | 287.9648 | 0.12398 | 319.2611 | 3 | 253719.2478 | 1640258.5894 | 1893977.8372 | 0 | 0 | NORMAL
0.097947 | 287.9648 | 0.12398 | 319.2611 | 4 | 397346.3791 | 2187011.4525 | 2584357.8316 | 0 | 0 | NORMAL
0.097947 | 294.2611 | 0.12398 | 285.9278 | 1 | 45675.9584 | 526711.3514 | 572387.3098 | 0 | 0 | NORMAL
0.097947 | 294.2611 | 0.12398 | 285.9278 | 2 | 97530.5003 | 1053422.7028 | 1150953.203 | 0 | 0 | NORMAL
0.097947 | 294.2611 | 0.12398 | 285.9278 | 3 | 172197.0005 | 1580134.0541 | 1752331.0547 | 0 | 0 | NORMAL
0.097947 | 294.2611 | 0.12398 | 285.9278 | 4 | 269675.4592 | 2106845.4055 | 2376520.8647 | 0 | 0 | NORMAL
0.097947 | 294.2611 | 0.12398 | 297.0389 | 1 | 59637.7661 | 571360.1382 | 630997.9042 | 0 | 0 | NORMAL
0.097947 | 294.2611 | 0.12398 | 297.0389 | 2 | 127342.7282 | 1142720.2763 | 1270063.0045 | 0 | 0 | NORMAL
0.097947 | 294.2611 | 0.12398 | 297.0389 | 3 | 224832.5988 | 1714080.4145 | 1938913.0132 | 0 | 0 | NORMAL
0.097947 | 294.2611 | 0.12398 | 297.0389 | 4 | 352107.3777 | 2285440.5526 | 2637547.9304 | 0 | 0 | NORMAL
0.097947 | 294.2611 | 0.12398 | 308.15 | 1 | 68032.2639 | 577627.4639 | 645659.7278 | 0 | 0 | NORMAL
0.097947 | 294.2611 | 0.12398 | 308.15 | 2 | 145267.2469 | 1155254.9277 | 1300522.1747 | 0 | 0 | NORMAL
0.097947 | 294.2611 | 0.12398 | 308.15 | 3 | 256479.6051 | 1732882.3916 | 1989361.9967 | 0 | 0 | NORMAL
0.097947 | 294.2611 | 0.12398 | 308.15 | 4 | 401669.3384 | 2310509.8555 | 2712179.1939 | 0 | 0 | NORMAL
0.097947 | 294.2611 | 0.12398 | 319.2611 | 1 | 69236.412 | 545513.3285 | 614749.7405 | 0 | 0 | NORMAL
0.097947 | 294.2611 | 0.12398 | 319.2611 | 2 | 147838.4281 | 1091026.657 | 1238865.0851 | 0 | 0 | NORMAL
0.097947 | 294.2611 | 0.12398 | 319.2611 | 3 | 261019.2074 | 1636539.9855 | 1897559.1929 | 0 | 0 | NORMAL
0.097947 | 294.2611 | 0.12398 | 319.2611 | 4 | 408778.7499 | 2182053.314 | 2590832.0639 | 0 | 0 | NORMAL
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on J3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).
Note on K3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation