## RS0001
RS0001: Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 3.0.0 |  | ✓
| description | ASHRAE 90.1-2022 Appendix J curve set 'R': 0.0-150.0 ton, 5.06 COP, 7.99 IPLV liquid-cooled, centrifugal compressor chiller |  | ✓
| id | 038354a7-fbf9-422f-93a1-7a2e2a4424d5 |  | ✓
| data_timestamp | 2025-02-18T13:40Z |  | ✓
| data_version | 3 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2022 Appendix J curve set 'R' for Energy Cost Budget (ECB) Path B
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | CENTRIFUGAL
performance |  |  |  | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| cycling_degradation_coefficient | 0 | - | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
performance.performance_map_evaporator_liquid_pressure_differential |  | $performance_map_evaporator_liqu |  | ✓
| condenser_type | LIQUID |  | ✓
performance.condenser_liquid_type
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| condenser_fouling_factor | 0 | m2-K/W
performance.performance_map_condenser_liquid_pressure_differential |  | $performance_map_condenser_liqui
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
performance.scaling
| maximum | 2 | -
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on B20: Type of compressor speed control
Note on B21: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A22: Type of liquid in evaporator
Note on A23: An array of all liquid components within the liquid mixture
Note on B24: Defines whether concentration is defined on a volume or mass basis
Note on B25: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on A26: Data group describing the liquid pressure differential through the evaporator
Note on B27: Heat rejection method of the condenser
Note on A28: Type of liquid in condenser
Note on A29: An array of all liquid components within the liquid mixture
Note on B30: Defines whether concentration is defined on a volume or mass basis
Note on B31: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on A32: Data group describing the liquid pressure differential through the condenser
Note on A33: Data group describing cooling performance over a range of conditions
Note on A34: Data group describing standby performance
Note on A35: Specifies the range the performance data can be scaled to represent different capacity equipment
Note on B36: Maximum scaling factor

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_evaporator_liqu
performance.performance_map_evaporator_liquid_pressure_differential
grid_variables |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | evaporator_liquid_differential_pressure
m3/s | K | Pa
0.011302 | 275.3722 | 15000
0.011302 | 281.6685 | 15000
0.011302 | 287.9648 | 15000
0.011302 | 294.2611 | 15000
Note on A2: Data group defining the grid variables for the evaporator liquid pressure differential
Note on C2: Data group defining the lookup variables for the evaporator liquid pressure differential
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Pressure difference across the evaporator

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_condenser_liqui
performance.performance_map_condenser_liquid_pressure_differential
grid_variables |  | lookup_variables
condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | condenser_liquid_differential_pressure
m3/s | K | Pa
0.014688 | 285.9278 | 15000
0.014688 | 297.0389 | 15000
0.014688 | 308.15 | 15000
0.014688 | 319.2611 | 15000
Note on A2: Data group defining the grid variables for the condenser liquid pressure differential
Note on C2: Data group defining the lookup variables for the condenser liquid pressure differential
Note on A3: Condenser liquid flow
Note on B3: Entering condenser liquid temperature
Note on C3: Pressure difference across the condenser

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | oil_cooler_heat | auxiliary_heat | operation_state
m3/s | K | m3/s | K | - | W | W | W | W | W | -
0.011302 | 275.3722 | 0.014688 | 285.9278 | 1 | 6543.9279 | 63367.011 | 69910.9389 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 0.014688 | 285.9278 | 2 | 14396.3142 | 126734.0219 | 141130.3361 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 0.014688 | 285.9278 | 3 | 26696.1542 | 190101.0329 | 216797.1872 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 0.014688 | 285.9278 | 4 | 43443.4481 | 253468.0439 | 296911.492 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 0.014688 | 297.0389 | 1 | 7177.7828 | 58229.8814 | 65407.6642 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 0.014688 | 297.0389 | 2 | 15790.7632 | 116459.7629 | 132250.526 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 0.014688 | 297.0389 | 3 | 29281.9845 | 174689.6443 | 203971.6288 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 0.014688 | 297.0389 | 4 | 47651.4467 | 232919.5258 | 280570.9725 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 0.014688 | 308.15 | 1 | 7088.5555 | 53304.4144 | 60392.9699 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 0.014688 | 308.15 | 2 | 15594.4676 | 106608.8287 | 122203.2964 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 0.014688 | 308.15 | 3 | 28917.9791 | 159913.2431 | 188831.2222 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 0.014688 | 308.15 | 4 | 47059.0899 | 213217.6575 | 260276.7474 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 0.014688 | 319.2611 | 1 | 6434.3148 | 48590.6098 | 55024.9246 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 0.014688 | 319.2611 | 2 | 14155.1708 | 97181.2196 | 111336.3903 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 0.014688 | 319.2611 | 3 | 26248.9841 | 145771.8293 | 172020.8135 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 0.014688 | 319.2611 | 4 | 42715.7548 | 194362.4391 | 237078.1939 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 0.014688 | 285.9278 | 1 | 6659.7731 | 74129.7662 | 80789.5393 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 0.014688 | 285.9278 | 2 | 14651.1677 | 148259.5324 | 162910.7002 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 0.014688 | 285.9278 | 3 | 27168.7481 | 222389.2987 | 249558.0467 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 0.014688 | 285.9278 | 4 | 44212.5141 | 296519.0649 | 340731.579 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 0.014688 | 297.0389 | 1 | 7745.2038 | 70505.752 | 78250.9558 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 0.014688 | 297.0389 | 2 | 17039.061 | 141011.504 | 158050.5649 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 0.014688 | 297.0389 | 3 | 31596.7959 | 211517.2559 | 243114.0518 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 0.014688 | 297.0389 | 4 | 51418.4083 | 282023.0079 | 333441.4162 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 0.014688 | 308.15 | 1 | 8023.3601 | 67093.4002 | 75116.7603 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 0.014688 | 308.15 | 2 | 17650.9909 | 134186.8004 | 151837.7913 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 0.014688 | 308.15 | 3 | 32731.5429 | 201280.2006 | 234011.7436 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 0.014688 | 308.15 | 4 | 53265.0161 | 268373.6008 | 321638.617 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 0.014688 | 319.2611 | 1 | 7605.6575 | 63892.7109 | 71498.3684 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 0.014688 | 319.2611 | 2 | 16732.0661 | 127785.4218 | 144517.4879 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 0.014688 | 319.2611 | 3 | 31027.5124 | 191678.1327 | 222705.6451 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 0.014688 | 319.2611 | 4 | 50491.9964 | 255570.8436 | 306062.84 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 0.014688 | 285.9278 | 1 | 6507.1108 | 75581.0191 | 82088.1299 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 0.014688 | 285.9278 | 2 | 14315.3183 | 151162.0382 | 165477.3565 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 0.014688 | 285.9278 | 3 | 26545.9575 | 226743.0573 | 253289.0148 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 0.014688 | 285.9278 | 4 | 43199.0285 | 302324.0763 | 345523.1048 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 0.014688 | 297.0389 | 1 | 7796.9317 | 73470.1201 | 81267.0518 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 0.014688 | 297.0389 | 2 | 17152.8598 | 146940.2403 | 164093.1001 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 0.014688 | 297.0389 | 3 | 31807.8215 | 220410.3604 | 252218.1819 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 0.014688 | 297.0389 | 4 | 51761.8166 | 293880.4805 | 345642.2971 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 0.014688 | 308.15 | 1 | 8293.1575 | 71570.8837 | 79864.0412 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 0.014688 | 308.15 | 2 | 18244.5319 | 143141.7673 | 161386.2992 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 0.014688 | 308.15 | 3 | 33832.19 | 214712.651 | 248544.841 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 0.014688 | 308.15 | 4 | 55056.1319 | 286283.5346 | 341339.6665 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 0.014688 | 319.2611 | 1 | 8060.5507 | 69883.3096 | 77943.8603 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 0.014688 | 319.2611 | 2 | 17732.8084 | 139766.6193 | 157499.4276 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 0.014688 | 319.2611 | 3 | 32883.2631 | 209649.9289 | 242533.192 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 0.014688 | 319.2611 | 4 | 53511.9149 | 279533.2386 | 333045.1534 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 0.014688 | 285.9278 | 1 | 6232.7229 | 67720.7696 | 73953.4925 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 0.014688 | 285.9278 | 2 | 13711.6787 | 135441.5391 | 149153.2179 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 0.014688 | 285.9278 | 3 | 25426.5839 | 203162.3087 | 228588.8926 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 0.014688 | 285.9278 | 4 | 41377.4383 | 270883.0783 | 312260.5166 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 0.014688 | 297.0389 | 1 | 7523.2515 | 67122.9859 | 74646.2374 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 0.014688 | 297.0389 | 2 | 16550.7772 | 134245.9718 | 150796.749 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 0.014688 | 297.0389 | 3 | 30691.3349 | 201368.9577 | 232060.2926 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 0.014688 | 297.0389 | 4 | 49944.9247 | 268491.9436 | 318436.8683 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 0.014688 | 308.15 | 1 | 8131.7361 | 66736.8647 | 74868.6008 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 0.014688 | 308.15 | 2 | 17889.4127 | 133473.7294 | 151363.1421 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 0.014688 | 308.15 | 3 | 33173.6662 | 200210.5942 | 233384.2603 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 0.014688 | 308.15 | 4 | 53984.4964 | 266947.4589 | 320931.9553 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 0.014688 | 319.2611 | 1 | 8076.2857 | 66562.406 | 74638.6917 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 0.014688 | 319.2611 | 2 | 17767.4246 | 133124.812 | 150892.2366 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 0.014688 | 319.2611 | 3 | 32947.4546 | 199687.218 | 232634.6726 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 0.014688 | 319.2611 | 4 | 53616.3756 | 266249.624 | 319865.9996 | 0 | 0 | NORMAL
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on J3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).
Note on K3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation