## RS0001
RS0001: Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 3.0.0 |  | ✓
| description | ASHRAE 90.1-2022 Appendix J curve set 'S': 150.0-300.0 ton, 5.54 COP, 8.79 IPLV liquid-cooled, centrifugal compressor chiller |  | ✓
| id | c7013fe1-2d02-4503-9e02-9664bf64f906 |  | ✓
| data_timestamp | 2025-02-18T13:40Z |  | ✓
| data_version | 3 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2022 Appendix J curve set 'S' for Energy Cost Budget (ECB) Path B
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | CENTRIFUGAL
performance |  |  |  | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| cycling_degradation_coefficient | 0 | - | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
performance.performance_map_evaporator_liquid_pressure_differential |  | $performance_map_evaporator_liqu |  | ✓
| condenser_type | LIQUID |  | ✓
performance.condenser_liquid_type
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| condenser_fouling_factor | 0 | m2-K/W
performance.performance_map_condenser_liquid_pressure_differential |  | $performance_map_condenser_liqui
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
performance.scaling
| minimum | 0.66667 | -
| maximum | 1.3333 | -
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on B20: Type of compressor speed control
Note on B21: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A22: Type of liquid in evaporator
Note on A23: An array of all liquid components within the liquid mixture
Note on B24: Defines whether concentration is defined on a volume or mass basis
Note on B25: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on A26: Data group describing the liquid pressure differential through the evaporator
Note on B27: Heat rejection method of the condenser
Note on A28: Type of liquid in condenser
Note on A29: An array of all liquid components within the liquid mixture
Note on B30: Defines whether concentration is defined on a volume or mass basis
Note on B31: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on A32: Data group describing the liquid pressure differential through the condenser
Note on A33: Data group describing cooling performance over a range of conditions
Note on A34: Data group describing standby performance
Note on A35: Specifies the range the performance data can be scaled to represent different capacity equipment
Note on B36: Minimum scaling factor
Note on B37: Maximum scaling factor

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_evaporator_liqu
performance.performance_map_evaporator_liquid_pressure_differential
grid_variables |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | evaporator_liquid_differential_pressure
m3/s | K | Pa
0.033905 | 275.3722 | 15000
0.033905 | 281.6685 | 15000
0.033905 | 287.9648 | 15000
0.033905 | 294.2611 | 15000
Note on A2: Data group defining the grid variables for the evaporator liquid pressure differential
Note on C2: Data group defining the lookup variables for the evaporator liquid pressure differential
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Pressure difference across the evaporator

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_condenser_liqui
performance.performance_map_condenser_liquid_pressure_differential
grid_variables |  | lookup_variables
condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | condenser_liquid_differential_pressure
m3/s | K | Pa
0.043438 | 285.9278 | 15000
0.043438 | 297.0389 | 15000
0.043438 | 308.15 | 15000
0.043438 | 319.2611 | 15000
Note on A2: Data group defining the grid variables for the condenser liquid pressure differential
Note on C2: Data group defining the lookup variables for the condenser liquid pressure differential
Note on A3: Condenser liquid flow
Note on B3: Entering condenser liquid temperature
Note on C3: Pressure difference across the condenser

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | oil_cooler_heat | auxiliary_heat | operation_state
m3/s | K | m3/s | K | - | W | W | W | W | W | -
0.033905 | 275.3722 | 0.043438 | 285.9278 | 1 | 17700.4653 | 192769.206 | 210469.6714 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043438 | 285.9278 | 2 | 39184.5275 | 385538.4121 | 424722.9396 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043438 | 285.9278 | 3 | 72037.3863 | 578307.6181 | 650345.0045 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043438 | 285.9278 | 4 | 116259.0417 | 771076.8242 | 887335.8659 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043438 | 297.0389 | 1 | 19636.8321 | 173950.1331 | 193586.9652 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043438 | 297.0389 | 2 | 43471.1727 | 347900.2662 | 391371.4389 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043438 | 297.0389 | 3 | 79918.0151 | 521850.3993 | 601768.4144 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043438 | 297.0389 | 4 | 128977.3593 | 695800.5324 | 824777.8917 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043438 | 308.15 | 1 | 17854.4704 | 148585.8053 | 166440.2757 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043438 | 308.15 | 2 | 39525.4573 | 297171.6107 | 336697.0679 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043438 | 308.15 | 3 | 72664.1563 | 445757.416 | 518421.5724 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043438 | 308.15 | 4 | 117270.5676 | 594343.2214 | 711613.789 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043438 | 319.2611 | 1 | 13259.9035 | 116676.2228 | 129936.1263 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043438 | 319.2611 | 2 | 29354.2031 | 233352.4455 | 262706.6486 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043438 | 319.2611 | 3 | 53965.1797 | 350028.6683 | 403993.848 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.043438 | 319.2611 | 4 | 87092.8334 | 466704.891 | 553797.7244 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043438 | 285.9278 | 1 | 17471.3804 | 224275.634 | 241747.0144 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043438 | 285.9278 | 2 | 38677.3891 | 448551.2681 | 487228.6572 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043438 | 285.9278 | 3 | 71105.0559 | 672826.9021 | 743931.958 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043438 | 285.9278 | 4 | 114754.3808 | 897102.5361 | 1011856.917 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043438 | 297.0389 | 1 | 21660.7515 | 215268.7447 | 236929.4962 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043438 | 297.0389 | 2 | 47951.6383 | 430537.4894 | 478489.1277 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043438 | 297.0389 | 3 | 88154.966 | 645806.2341 | 733961.2001 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043438 | 297.0389 | 4 | 142270.7346 | 861074.9788 | 1003345.7135 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043438 | 308.15 | 1 | 21879.3069 | 199716.6006 | 221595.9075 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043438 | 308.15 | 2 | 48435.467 | 399433.2011 | 447868.6681 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043438 | 308.15 | 3 | 89044.4436 | 599149.8017 | 688194.2452 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043438 | 308.15 | 4 | 143706.2366 | 798866.4022 | 942572.6388 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043438 | 319.2611 | 1 | 18595.1255 | 177619.2016 | 196214.3271 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043438 | 319.2611 | 2 | 41165.0877 | 355238.4032 | 396403.4909 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043438 | 319.2611 | 3 | 75678.476 | 532857.6048 | 608536.0808 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.043438 | 319.2611 | 4 | 122135.2904 | 710476.8064 | 832612.0968 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043438 | 285.9278 | 1 | 15946.992 | 226639.8305 | 242586.8225 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043438 | 285.9278 | 2 | 35302.7637 | 453279.6611 | 488582.4248 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043438 | 285.9278 | 3 | 64901.0972 | 679919.4916 | 744820.5889 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043438 | 285.9278 | 4 | 104741.9924 | 906559.3222 | 1011301.3146 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043438 | 297.0389 | 1 | 21547.723 | 227445.1248 | 248992.8479 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043438 | 297.0389 | 2 | 47701.4209 | 454890.2497 | 502591.6705 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043438 | 297.0389 | 3 | 87694.9628 | 682335.3745 | 770030.3373 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043438 | 297.0389 | 4 | 141528.3488 | 909780.4993 | 1051308.8482 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043438 | 308.15 | 1 | 23350.6222 | 221705.1643 | 245055.7865 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043438 | 308.15 | 2 | 51692.6013 | 443410.3286 | 495102.93 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043438 | 308.15 | 3 | 95032.4051 | 665115.4929 | 760147.898 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043438 | 308.15 | 4 | 153370.0335 | 886820.6572 | 1040190.6907 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043438 | 319.2611 | 1 | 21385.3236 | 209419.949 | 230805.2726 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043438 | 319.2611 | 2 | 47341.908 | 418839.8979 | 466181.8059 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043438 | 319.2611 | 3 | 87034.0292 | 628259.8469 | 715293.8761 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.043438 | 319.2611 | 4 | 140461.6874 | 837679.7959 | 978141.4832 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043438 | 285.9278 | 1 | 13831.646 | 199861.7956 | 213693.4416 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043438 | 285.9278 | 2 | 30619.902 | 399723.5912 | 430343.4932 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043438 | 285.9278 | 3 | 56292.0583 | 599585.3868 | 655877.4451 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043438 | 285.9278 | 4 | 90848.115 | 799447.1823 | 890295.2974 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043438 | 297.0389 | 1 | 20045.2765 | 210479.2735 | 230524.55 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043438 | 297.0389 | 2 | 44375.3695 | 420958.547 | 465333.9164 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043438 | 297.0389 | 3 | 81580.3031 | 631437.8205 | 713018.1236 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043438 | 297.0389 | 4 | 131660.0775 | 841917.094 | 973577.1714 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043438 | 308.15 | 1 | 23059.1296 | 214551.4966 | 237610.6262 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043438 | 308.15 | 2 | 51047.3077 | 429102.9932 | 480150.3008 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043438 | 308.15 | 3 | 93846.0881 | 643654.4897 | 737500.5778 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043438 | 308.15 | 4 | 151455.471 | 858205.9863 | 1009661.4573 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043438 | 319.2611 | 1 | 22464.395 | 212078.4649 | 234542.8599 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043438 | 319.2611 | 2 | 49730.7098 | 424156.9297 | 473887.6395 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043438 | 319.2611 | 3 | 91425.6361 | 636235.3946 | 727661.0306 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.043438 | 319.2611 | 4 | 147549.1739 | 848313.8594 | 995863.0333 | 0 | 0 | NORMAL
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on J3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).
Note on K3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation