## RS0001
RS0001: Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 3.0.0 |  | ✓
| description | ASHRAE 90.1-2022 Appendix J curve set 'T': 300.0-400.0 ton, 5.91 COP, 9.02 IPLV liquid-cooled, centrifugal compressor chiller |  | ✓
| id | fb36d102-86a1-4ff3-9ef4-8b508222c611 |  | ✓
| data_timestamp | 2025-02-18T13:40Z |  | ✓
| data_version | 3 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2022 Appendix J curve set 'T' for Energy Cost Budget (ECB) Path B
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | CENTRIFUGAL
performance |  |  |  | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| cycling_degradation_coefficient | 0 | - | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
performance.performance_map_evaporator_liquid_pressure_differential |  | $performance_map_evaporator_liqu |  | ✓
| condenser_type | LIQUID |  | ✓
performance.condenser_liquid_type
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| condenser_fouling_factor | 0 | m2-K/W
performance.performance_map_condenser_liquid_pressure_differential |  | $performance_map_condenser_liqui
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
performance.scaling
| minimum | 0.85714 | -
| maximum | 1.1429 | -
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on B20: Type of compressor speed control
Note on B21: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A22: Type of liquid in evaporator
Note on A23: An array of all liquid components within the liquid mixture
Note on B24: Defines whether concentration is defined on a volume or mass basis
Note on B25: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on A26: Data group describing the liquid pressure differential through the evaporator
Note on B27: Heat rejection method of the condenser
Note on A28: Type of liquid in condenser
Note on A29: An array of all liquid components within the liquid mixture
Note on B30: Defines whether concentration is defined on a volume or mass basis
Note on B31: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on A32: Data group describing the liquid pressure differential through the condenser
Note on A33: Data group describing cooling performance over a range of conditions
Note on A34: Data group describing standby performance
Note on A35: Specifies the range the performance data can be scaled to represent different capacity equipment
Note on B36: Minimum scaling factor
Note on B37: Maximum scaling factor

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_evaporator_liqu
performance.performance_map_evaporator_liquid_pressure_differential
grid_variables |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | evaporator_liquid_differential_pressure
m3/s | K | Pa
0.052741 | 275.3722 | 15000
0.052741 | 281.6685 | 15000
0.052741 | 287.9648 | 15000
0.052741 | 294.2611 | 15000
Note on A2: Data group defining the grid variables for the evaporator liquid pressure differential
Note on C2: Data group defining the lookup variables for the evaporator liquid pressure differential
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Pressure difference across the evaporator

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_condenser_liqui
performance.performance_map_condenser_liquid_pressure_differential
grid_variables |  | lookup_variables
condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | condenser_liquid_differential_pressure
m3/s | K | Pa
0.066919 | 285.9278 | 15000
0.066919 | 297.0389 | 15000
0.066919 | 308.15 | 15000
0.066919 | 319.2611 | 15000
Note on A2: Data group defining the grid variables for the condenser liquid pressure differential
Note on C2: Data group defining the lookup variables for the condenser liquid pressure differential
Note on A3: Condenser liquid flow
Note on B3: Entering condenser liquid temperature
Note on C3: Pressure difference across the condenser

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | oil_cooler_heat | auxiliary_heat | operation_state
m3/s | K | m3/s | K | - | W | W | W | W | W | -
0.052741 | 275.3722 | 0.066919 | 285.9278 | 1 | 29862.7752 | 311545.3229 | 341408.0982 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.066919 | 285.9278 | 2 | 61988.1569 | 623090.6459 | 685078.8028 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.066919 | 285.9278 | 3 | 111025.0884 | 934635.9688 | 1045661.0572 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.066919 | 285.9278 | 4 | 176973.5696 | 1246181.2918 | 1423154.8613 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.066919 | 297.0389 | 1 | 32886.0072 | 278580.0331 | 311466.0403 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.066919 | 297.0389 | 2 | 68263.6814 | 557160.0662 | 625423.7476 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.066919 | 297.0389 | 3 | 122264.988 | 835740.0993 | 958005.0873 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.066919 | 297.0389 | 4 | 194889.9269 | 1114320.1324 | 1309210.0593 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.066919 | 308.15 | 1 | 30023.5167 | 233989.5892 | 264013.1059 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.066919 | 308.15 | 2 | 62321.8188 | 467979.1783 | 530300.9971 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.066919 | 308.15 | 3 | 111622.6999 | 701968.7675 | 813591.4674 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.066919 | 308.15 | 4 | 177926.16 | 935958.3567 | 1113884.5167 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.066919 | 319.2611 | 1 | 22513.5926 | 177773.9912 | 200287.5838 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.066919 | 319.2611 | 2 | 46732.9678 | 355547.9824 | 402280.9502 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.066919 | 319.2611 | 3 | 83701.9866 | 533321.9735 | 617023.9601 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.066919 | 319.2611 | 4 | 133420.649 | 711095.9647 | 844516.6137 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.066919 | 285.9278 | 1 | 29020.4883 | 355635.5855 | 384656.0738 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.066919 | 285.9278 | 2 | 60239.7657 | 711271.1711 | 771510.9368 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.066919 | 285.9278 | 3 | 107893.5984 | 1066906.7566 | 1174800.355 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.066919 | 285.9278 | 4 | 171981.9865 | 1422542.3421 | 1594524.3286 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.066919 | 297.0389 | 1 | 35035.605 | 336297.5596 | 371333.1646 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.066919 | 297.0389 | 2 | 72725.7452 | 672595.1193 | 745320.8645 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.066919 | 297.0389 | 3 | 130256.8538 | 1008892.6789 | 1139149.5327 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.066919 | 297.0389 | 4 | 207628.9306 | 1345190.2385 | 1552819.1691 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.066919 | 308.15 | 1 | 35060.5272 | 305334.3796 | 340394.9069 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.066919 | 308.15 | 2 | 72777.478 | 610668.7593 | 683446.2372 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.066919 | 308.15 | 3 | 130349.5106 | 916003.1389 | 1046352.6496 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.066919 | 308.15 | 4 | 207776.6253 | 1221337.5186 | 1429114.1439 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.066919 | 319.2611 | 1 | 29832.3492 | 262746.0456 | 292578.3948 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.066919 | 319.2611 | 2 | 61924.9996 | 525492.0912 | 587417.0908 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.066919 | 319.2611 | 3 | 110911.9692 | 788238.1368 | 899150.106 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.066919 | 319.2611 | 4 | 176793.258 | 1050984.1824 | 1227777.4404 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.066919 | 285.9278 | 1 | 26783.4818 | 357223.7107 | 384007.1926 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.066919 | 285.9278 | 2 | 55596.262 | 714447.4215 | 770043.6835 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.066919 | 285.9278 | 3 | 99576.7613 | 1071671.1322 | 1171247.8935 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.066919 | 285.9278 | 4 | 158724.9796 | 1428894.843 | 1587619.8226 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.066919 | 297.0389 | 1 | 34426.8377 | 351512.9488 | 385939.7865 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.066919 | 297.0389 | 2 | 71462.0863 | 703025.8976 | 774487.9839 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.066919 | 297.0389 | 3 | 127993.553 | 1054538.8464 | 1182532.3994 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.066919 | 297.0389 | 4 | 204021.2378 | 1406051.7951 | 1610073.033 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.066919 | 308.15 | 1 | 36414.9236 | 334177.0327 | 370591.9563 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.066919 | 308.15 | 2 | 75588.8889 | 668354.0655 | 743942.9544 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.066919 | 308.15 | 3 | 135384.9427 | 1002531.0982 | 1137916.0409 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.066919 | 308.15 | 4 | 215803.0848 | 1336708.131 | 1552511.2158 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.066919 | 319.2611 | 1 | 32983.639 | 305215.9626 | 338199.6017 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.066919 | 319.2611 | 2 | 68466.3424 | 610431.9253 | 678898.2677 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.066919 | 319.2611 | 3 | 122627.9679 | 915647.8879 | 1038275.8558 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.066919 | 319.2611 | 4 | 195468.5155 | 1220863.8506 | 1416332.366 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.066919 | 285.9278 | 1 | 24032.8212 | 316309.6986 | 340342.5197 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.066919 | 285.9278 | 2 | 49886.5319 | 632619.3972 | 682505.9291 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.066919 | 285.9278 | 3 | 89350.2387 | 948929.0958 | 1038279.3345 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.066919 | 285.9278 | 4 | 142423.9414 | 1265238.7943 | 1407662.7358 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.066919 | 297.0389 | 1 | 32203.6584 | 324226.2006 | 356429.859 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.066919 | 297.0389 | 2 | 66847.2846 | 648452.4011 | 715299.6857 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.066919 | 297.0389 | 3 | 119728.123 | 972678.6017 | 1092406.7247 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.066919 | 297.0389 | 4 | 190846.1738 | 1296904.8023 | 1487750.976 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.066919 | 308.15 | 1 | 35493.5467 | 320517.5485 | 356011.0951 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.066919 | 308.15 | 2 | 73676.3253 | 641035.0969 | 714711.4222 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.066919 | 308.15 | 3 | 131959.4086 | 961552.6454 | 1093512.054 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.066919 | 308.15 | 4 | 210342.7965 | 1282070.1939 | 1492412.9904 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.066919 | 319.2611 | 1 | 33637.1909 | 305183.7423 | 338820.9332 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.066919 | 319.2611 | 2 | 69822.9637 | 610367.4846 | 680190.4483 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.066919 | 319.2611 | 3 | 125057.7708 | 915551.2269 | 1040608.9977 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.066919 | 319.2611 | 4 | 199341.612 | 1220734.9692 | 1420076.5812 | 0 | 0 | NORMAL
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on J3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).
Note on K3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation