## RS0001
RS0001: Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 3.0.0 |  | ✓
| description | ASHRAE 90.1-2022 Appendix J curve set 'U': 400.0+ ton, 6.01 COP, 9.25 IPLV liquid-cooled, centrifugal compressor chiller |  | ✓
| id | d0dd49a6-2f3e-4b57-ad73-ef0e27459793 |  | ✓
| data_timestamp | 2025-02-18T13:40Z |  | ✓
| data_version | 3 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2022 Appendix J curve set 'U' for Energy Cost Budget (ECB) Path B
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | CENTRIFUGAL
performance |  |  |  | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| cycling_degradation_coefficient | 0 | - | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
performance.performance_map_evaporator_liquid_pressure_differential |  | $performance_map_evaporator_liqu |  | ✓
| condenser_type | LIQUID |  | ✓
performance.condenser_liquid_type
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| condenser_fouling_factor | 0 | m2-K/W
performance.performance_map_condenser_liquid_pressure_differential |  | $performance_map_condenser_liqui
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
performance.scaling
| minimum | 0.88889 | -
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on B20: Type of compressor speed control
Note on B21: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A22: Type of liquid in evaporator
Note on A23: An array of all liquid components within the liquid mixture
Note on B24: Defines whether concentration is defined on a volume or mass basis
Note on B25: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on A26: Data group describing the liquid pressure differential through the evaporator
Note on B27: Heat rejection method of the condenser
Note on A28: Type of liquid in condenser
Note on A29: An array of all liquid components within the liquid mixture
Note on B30: Defines whether concentration is defined on a volume or mass basis
Note on B31: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on A32: Data group describing the liquid pressure differential through the condenser
Note on A33: Data group describing cooling performance over a range of conditions
Note on A34: Data group describing standby performance
Note on A35: Specifies the range the performance data can be scaled to represent different capacity equipment
Note on B36: Minimum scaling factor

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_evaporator_liqu
performance.performance_map_evaporator_liquid_pressure_differential
grid_variables |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | evaporator_liquid_differential_pressure
m3/s | K | Pa
0.067809 | 275.3722 | 15000
0.067809 | 281.6685 | 15000
0.067809 | 287.9648 | 15000
0.067809 | 294.2611 | 15000
Note on A2: Data group defining the grid variables for the evaporator liquid pressure differential
Note on C2: Data group defining the lookup variables for the evaporator liquid pressure differential
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Pressure difference across the evaporator

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_condenser_liqui
performance.performance_map_condenser_liquid_pressure_differential
grid_variables |  | lookup_variables
condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | condenser_liquid_differential_pressure
m3/s | K | Pa
0.085829 | 285.9278 | 15000
0.085829 | 297.0389 | 15000
0.085829 | 308.15 | 15000
0.085829 | 319.2611 | 15000
Note on A2: Data group defining the grid variables for the condenser liquid pressure differential
Note on C2: Data group defining the lookup variables for the condenser liquid pressure differential
Note on A3: Condenser liquid flow
Note on B3: Entering condenser liquid temperature
Note on C3: Pressure difference across the condenser

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | oil_cooler_heat | auxiliary_heat | operation_state
m3/s | K | m3/s | K | - | W | W | W | W | W | -
0.067809 | 275.3722 | 0.085829 | 285.9278 | 1 | 33483.4938 | 382012.3563 | 415495.8501 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.085829 | 285.9278 | 2 | 74149.8967 | 764024.7127 | 838174.6093 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.085829 | 285.9278 | 3 | 134575.2636 | 1146037.069 | 1280612.3326 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.085829 | 285.9278 | 4 | 214759.5944 | 1528049.4253 | 1742809.0198 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.085829 | 297.0389 | 1 | 35848.1563 | 338733.08 | 374581.2363 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.085829 | 297.0389 | 2 | 79386.4913 | 677466.16 | 756852.6513 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.085829 | 297.0389 | 3 | 144079.2026 | 1016199.24 | 1160278.4426 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.085829 | 297.0389 | 4 | 229926.2904 | 1354932.32 | 1584858.6104 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.085829 | 308.15 | 1 | 32389.2209 | 285294.0051 | 317683.2261 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.085829 | 308.15 | 2 | 71726.6066 | 570588.0103 | 642314.6169 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.085829 | 308.15 | 3 | 130177.2142 | 855882.0154 | 986059.2297 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.085829 | 308.15 | 4 | 207741.0439 | 1141176.0206 | 1348917.0645 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.085829 | 319.2611 | 1 | 24552.2487 | 221695.1318 | 246247.3805 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.085829 | 319.2611 | 2 | 54371.4679 | 443390.2636 | 497761.7315 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.085829 | 319.2611 | 3 | 98679.2289 | 665085.3953 | 763764.6243 | 0 | 0 | NORMAL
0.067809 | 275.3722 | 0.085829 | 319.2611 | 4 | 157475.5317 | 886780.5271 | 1044256.0588 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.085829 | 285.9278 | 1 | 36073.4702 | 466432.1954 | 502505.6657 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.085829 | 285.9278 | 2 | 79885.4537 | 932864.3909 | 1012749.8446 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.085829 | 285.9278 | 3 | 144984.7737 | 1399296.5863 | 1544281.36 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.085829 | 285.9278 | 4 | 231371.4302 | 1865728.7817 | 2097100.2119 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.085829 | 297.0389 | 1 | 42043.7028 | 437269.1776 | 479312.8804 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.085829 | 297.0389 | 2 | 93106.6584 | 874538.3552 | 967645.0137 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.085829 | 297.0389 | 3 | 168980.048 | 1311807.5328 | 1480787.5809 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.085829 | 297.0389 | 4 | 269663.8715 | 1749076.7105 | 2018740.582 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.085829 | 308.15 | 1 | 41578.0124 | 397946.3613 | 439524.3736 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.085829 | 308.15 | 2 | 92075.3773 | 795892.7226 | 887968.0998 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.085829 | 308.15 | 3 | 167108.3673 | 1193839.0838 | 1360947.4511 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.085829 | 308.15 | 4 | 266676.9823 | 1591785.4451 | 1858462.4274 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.085829 | 319.2611 | 1 | 35658.8653 | 348463.7464 | 384122.6117 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.085829 | 319.2611 | 2 | 78967.3024 | 696927.4929 | 775894.7953 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.085829 | 319.2611 | 3 | 143318.4133 | 1045391.2393 | 1188709.6526 | 0 | 0 | NORMAL
0.067809 | 281.6685 | 0.085829 | 319.2611 | 4 | 228712.198 | 1393854.9857 | 1622567.1837 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.085829 | 285.9278 | 1 | 34750.8557 | 475973.1255 | 510723.9812 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.085829 | 285.9278 | 2 | 76956.4963 | 951946.2509 | 1028902.7472 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.085829 | 285.9278 | 3 | 139668.9845 | 1427919.3764 | 1567588.3609 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.085829 | 285.9278 | 4 | 222888.3205 | 1903892.5018 | 2126780.8223 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.085829 | 297.0389 | 1 | 42614.1395 | 460926.3662 | 503540.5057 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.085829 | 297.0389 | 2 | 94369.9026 | 921852.7323 | 1016222.6349 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.085829 | 297.0389 | 3 | 171272.7203 | 1382779.0985 | 1554051.8188 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.085829 | 297.0389 | 4 | 273322.5927 | 1843705.4646 | 2117028.0573 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.085829 | 308.15 | 1 | 44188.8438 | 435719.8083 | 479908.6522 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.085829 | 308.15 | 2 | 97857.1181 | 871439.6167 | 969296.7348 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.085829 | 308.15 | 3 | 177601.6968 | 1307159.425 | 1484761.1218 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.085829 | 308.15 | 4 | 283422.5798 | 1742879.2334 | 2026301.8132 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.085829 | 319.2611 | 1 | 39994.3401 | 400353.452 | 440347.7921 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.085829 | 319.2611 | 2 | 88568.302 | 800706.904 | 889275.206 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.085829 | 319.2611 | 3 | 160743.3472 | 1201060.356 | 1361803.7032 | 0 | 0 | NORMAL
0.067809 | 287.9648 | 0.085829 | 319.2611 | 4 | 256519.4757 | 1601413.808 | 1857933.2837 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.085829 | 285.9278 | 1 | 30659.334 | 410635.1464 | 441294.4804 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.085829 | 285.9278 | 2 | 67895.7359 | 821270.2928 | 889166.0287 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.085829 | 285.9278 | 3 | 123224.5353 | 1231905.4392 | 1355129.9745 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.085829 | 285.9278 | 4 | 196645.7321 | 1642540.5856 | 1839186.3177 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.085829 | 297.0389 | 1 | 38814.5919 | 409704.6456 | 448519.2375 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.085829 | 297.0389 | 2 | 85955.7249 | 819409.2912 | 905365.0162 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.085829 | 297.0389 | 3 | 156001.7593 | 1229113.9369 | 1385115.6962 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.085829 | 297.0389 | 4 | 248952.6952 | 1638818.5825 | 1887771.2777 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.085829 | 308.15 | 1 | 41588.2822 | 398614.3463 | 440202.6285 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.085829 | 308.15 | 2 | 92098.12 | 797228.6927 | 889326.8127 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.085829 | 308.15 | 3 | 167149.6433 | 1195843.039 | 1362992.6823 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.085829 | 308.15 | 4 | 266742.852 | 1594457.3853 | 1861200.2373 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.085829 | 319.2611 | 1 | 39036.6816 | 377364.2485 | 416400.9301 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.085829 | 319.2611 | 2 | 86447.5472 | 754728.497 | 841176.0442 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.085829 | 319.2611 | 3 | 156894.3716 | 1132092.7455 | 1288987.1172 | 0 | 0 | NORMAL
0.067809 | 294.2611 | 0.085829 | 319.2611 | 4 | 250377.155 | 1509456.994 | 1759834.149 | 0 | 0 | NORMAL
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on J3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).
Note on K3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation