## RS0001
RS0001: Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 3.0.0 |  | ✓
| description | ASHRAE 90.1-2022 Appendix J curve set 'V': 0.0-150.0 ton, 4.45 COP, 5.20 IPLV liquid-cooled, positive displacement compressor chiller |  | ✓
| id | 0f3f19d2-3b61-465e-b72d-cf57d0860d09 |  | ✓
| data_timestamp | 2025-02-18T13:40Z |  | ✓
| data_version | 3 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2022 Appendix J curve set 'V' for Performance Rating Method (PRM)
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | SCROLL
performance |  |  |  | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| cycling_degradation_coefficient | 0 | - | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
performance.performance_map_evaporator_liquid_pressure_differential |  | $performance_map_evaporator_liqu |  | ✓
| condenser_type | LIQUID |  | ✓
performance.condenser_liquid_type
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| condenser_fouling_factor | 0 | m2-K/W
performance.performance_map_condenser_liquid_pressure_differential |  | $performance_map_condenser_liqui
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
performance.scaling
| maximum | 2 | -
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on B20: Type of compressor speed control
Note on B21: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A22: Type of liquid in evaporator
Note on A23: An array of all liquid components within the liquid mixture
Note on B24: Defines whether concentration is defined on a volume or mass basis
Note on B25: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on A26: Data group describing the liquid pressure differential through the evaporator
Note on B27: Heat rejection method of the condenser
Note on A28: Type of liquid in condenser
Note on A29: An array of all liquid components within the liquid mixture
Note on B30: Defines whether concentration is defined on a volume or mass basis
Note on B31: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on A32: Data group describing the liquid pressure differential through the condenser
Note on A33: Data group describing cooling performance over a range of conditions
Note on A34: Data group describing standby performance
Note on A35: Specifies the range the performance data can be scaled to represent different capacity equipment
Note on B36: Maximum scaling factor

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_evaporator_liqu
performance.performance_map_evaporator_liquid_pressure_differential
grid_variables |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | evaporator_liquid_differential_pressure
m3/s | K | Pa
0.011302 | 275.3722 | 15000
0.011302 | 281.6685 | 15000
0.011302 | 287.9648 | 15000
0.011302 | 294.2611 | 15000
Note on A2: Data group defining the grid variables for the evaporator liquid pressure differential
Note on C2: Data group defining the lookup variables for the evaporator liquid pressure differential
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Pressure difference across the evaporator

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_condenser_liqui
performance.performance_map_condenser_liquid_pressure_differential
grid_variables |  | lookup_variables
condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | condenser_liquid_differential_pressure
m3/s | K | Pa
0.015021 | 285.9278 | 15000
0.015021 | 297.0389 | 15000
0.015021 | 308.15 | 15000
0.015021 | 319.2611 | 15000
Note on A2: Data group defining the grid variables for the condenser liquid pressure differential
Note on C2: Data group defining the lookup variables for the condenser liquid pressure differential
Note on A3: Condenser liquid flow
Note on B3: Entering condenser liquid temperature
Note on C3: Pressure difference across the condenser

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | oil_cooler_heat | auxiliary_heat | operation_state
m3/s | K | m3/s | K | - | W | W | W | W | W | -
0.011302 | 275.3722 | 0.015021 | 285.9278 | 1 | 16389.469 | 62041.9355 | 78431.4045 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 0.015021 | 285.9278 | 2 | 23096.6263 | 124083.8711 | 147180.4974 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 0.015021 | 285.9278 | 3 | 32395.9322 | 186125.8066 | 218521.7388 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 0.015021 | 285.9278 | 4 | 44287.3868 | 248167.7421 | 292455.1289 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 0.015021 | 297.0389 | 1 | 18871.7039 | 57562.425 | 76434.1289 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 0.015021 | 297.0389 | 2 | 26594.6805 | 115124.85 | 141719.5306 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 0.015021 | 297.0389 | 3 | 37302.3946 | 172687.275 | 209989.6696 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 0.015021 | 297.0389 | 4 | 50994.846 | 230249.7 | 281244.546 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 0.015021 | 308.15 | 1 | 21901.0342 | 50021.9495 | 71922.9837 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 0.015021 | 308.15 | 2 | 30863.7212 | 100043.8991 | 130907.6203 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 0.015021 | 308.15 | 3 | 43290.2627 | 150065.8486 | 193356.1114 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 0.015021 | 308.15 | 4 | 59180.6587 | 200087.7982 | 259268.4568 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 0.015021 | 319.2611 | 1 | 23420.1261 | 39420.5091 | 62840.6352 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 0.015021 | 319.2611 | 2 | 33004.4799 | 78841.0183 | 111845.4982 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 0.015021 | 319.2611 | 3 | 46292.9469 | 118261.5274 | 164554.4743 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 0.015021 | 319.2611 | 4 | 63285.5269 | 157682.0366 | 220967.5635 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 0.015021 | 285.9278 | 1 | 16836.0119 | 76830.9614 | 93666.9733 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 0.015021 | 285.9278 | 2 | 23725.9106 | 153661.9228 | 177387.8334 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 0.015021 | 285.9278 | 3 | 33278.5829 | 230492.8842 | 263771.4671 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 0.015021 | 285.9278 | 4 | 45494.0287 | 307323.8456 | 352817.8743 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 0.015021 | 297.0389 | 1 | 19834.6878 | 72443.714 | 92278.4018 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 0.015021 | 297.0389 | 2 | 27951.752 | 144887.428 | 172839.18 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 0.015021 | 297.0389 | 3 | 39205.8585 | 217331.142 | 256537.0005 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 0.015021 | 297.0389 | 4 | 53597.0074 | 289774.856 | 343371.8634 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 0.015021 | 308.15 | 1 | 24357.6626 | 64995.5017 | 89353.1643 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 0.015021 | 308.15 | 2 | 34325.6899 | 129991.0033 | 164316.6933 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 0.015021 | 308.15 | 3 | 48146.1106 | 194986.505 | 243132.6156 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 0.015021 | 308.15 | 4 | 65818.9246 | 259982.0067 | 325800.9313 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 0.015021 | 319.2611 | 1 | 28443.2122 | 54486.3244 | 82929.5366 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 0.015021 | 319.2611 | 2 | 40083.1926 | 108972.6488 | 149055.8414 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 0.015021 | 319.2611 | 3 | 56221.7344 | 163458.9732 | 219680.7076 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 0.015021 | 319.2611 | 4 | 76858.8377 | 217945.2976 | 294804.1352 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 0.015021 | 285.9278 | 1 | 17366.8565 | 79987.1446 | 97354.0011 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 0.015021 | 285.9278 | 2 | 24473.9957 | 159974.2892 | 184448.2849 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 0.015021 | 285.9278 | 3 | 34327.8666 | 239961.4338 | 274289.3004 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 0.015021 | 285.9278 | 4 | 46928.469 | 319948.5784 | 366877.0474 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 0.015021 | 297.0389 | 1 | 19889.5058 | 75692.1603 | 95581.6662 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 0.015021 | 297.0389 | 2 | 28029.0035 | 151384.3207 | 179413.3242 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 0.015021 | 297.0389 | 3 | 39314.2135 | 227076.481 | 266390.6945 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 0.015021 | 297.0389 | 4 | 53745.1358 | 302768.6413 | 356513.7771 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 0.015021 | 308.15 | 1 | 24240.0154 | 68336.2111 | 92576.2265 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 0.015021 | 308.15 | 2 | 34159.8973 | 136672.4222 | 170832.3196 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 0.015021 | 308.15 | 3 | 47913.5655 | 205008.6334 | 252922.1989 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 0.015021 | 308.15 | 4 | 65501.0201 | 273344.8445 | 338845.8646 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 0.015021 | 319.2611 | 1 | 28552.2707 | 57919.297 | 86471.5677 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 0.015021 | 319.2611 | 2 | 40236.8819 | 115838.594 | 156075.4758 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 0.015021 | 319.2611 | 3 | 56437.303 | 173757.8909 | 230195.1939 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 0.015021 | 319.2611 | 4 | 77153.5342 | 231677.1879 | 308830.7221 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 0.015021 | 285.9278 | 1 | 18459.5514 | 71510.4851 | 89970.0365 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 0.015021 | 285.9278 | 2 | 26013.8605 | 143020.9703 | 169034.8308 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 0.015021 | 285.9278 | 3 | 36487.7212 | 214531.4554 | 251019.1766 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 0.015021 | 285.9278 | 4 | 49881.1335 | 286041.9405 | 335923.074 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 0.015021 | 297.0389 | 1 | 19840.2655 | 67307.764 | 87148.0295 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 0.015021 | 297.0389 | 2 | 27959.6123 | 134615.528 | 162575.1403 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 0.015021 | 297.0389 | 3 | 39216.8836 | 201923.292 | 241140.1756 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 0.015021 | 297.0389 | 4 | 53612.0794 | 269231.056 | 322843.1354 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 0.015021 | 308.15 | 1 | 22678.759 | 60044.0779 | 82722.837 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 0.015021 | 308.15 | 2 | 31959.719 | 120088.1558 | 152047.8748 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 0.015021 | 308.15 | 3 | 44827.5378 | 180132.2337 | 224959.7715 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 0.015021 | 308.15 | 4 | 61282.2156 | 240176.3116 | 301458.5272 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 0.015021 | 319.2611 | 1 | 25204.5271 | 49719.4269 | 74923.954 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 0.015021 | 319.2611 | 2 | 35519.1217 | 99438.8538 | 134957.9754 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 0.015021 | 319.2611 | 3 | 49820.0491 | 149158.2807 | 198978.3298 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 0.015021 | 319.2611 | 4 | 68107.3095 | 198877.7076 | 266985.0171 | 0 | 0 | NORMAL
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on J3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).
Note on K3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation