## RS0001
RS0001: Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 3.0.0 |  | ✓
| description | ASHRAE 90.1-2022 Appendix J curve set 'X': 150.0-300.0 ton, 4.90 COP, 5.60 IPLV liquid-cooled, positive displacement compressor chiller |  | ✓
| id | 9abacfb5-01d3-474b-9656-0e2f4a524425 |  | ✓
| data_timestamp | 2025-02-18T13:40Z |  | ✓
| data_version | 3 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2022 Appendix J curve set 'X' for Performance Rating Method (PRM)
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | SCROLL
performance |  |  |  | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| cycling_degradation_coefficient | 0 | - | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
performance.performance_map_evaporator_liquid_pressure_differential |  | $performance_map_evaporator_liqu |  | ✓
| condenser_type | LIQUID |  | ✓
performance.condenser_liquid_type
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| condenser_fouling_factor | 0 | m2-K/W
performance.performance_map_condenser_liquid_pressure_differential |  | $performance_map_condenser_liqui
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
performance.scaling
| minimum | 0.66667 | -
| maximum | 1.3333 | -
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on B20: Type of compressor speed control
Note on B21: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A22: Type of liquid in evaporator
Note on A23: An array of all liquid components within the liquid mixture
Note on B24: Defines whether concentration is defined on a volume or mass basis
Note on B25: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on A26: Data group describing the liquid pressure differential through the evaporator
Note on B27: Heat rejection method of the condenser
Note on A28: Type of liquid in condenser
Note on A29: An array of all liquid components within the liquid mixture
Note on B30: Defines whether concentration is defined on a volume or mass basis
Note on B31: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on A32: Data group describing the liquid pressure differential through the condenser
Note on A33: Data group describing cooling performance over a range of conditions
Note on A34: Data group describing standby performance
Note on A35: Specifies the range the performance data can be scaled to represent different capacity equipment
Note on B36: Minimum scaling factor
Note on B37: Maximum scaling factor

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_evaporator_liqu
performance.performance_map_evaporator_liquid_pressure_differential
grid_variables |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | evaporator_liquid_differential_pressure
m3/s | K | Pa
0.033905 | 275.3722 | 15000
0.033905 | 281.6685 | 15000
0.033905 | 287.9648 | 15000
0.033905 | 294.2611 | 15000
Note on A2: Data group defining the grid variables for the evaporator liquid pressure differential
Note on C2: Data group defining the lookup variables for the evaporator liquid pressure differential
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Pressure difference across the evaporator

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_condenser_liqui
performance.performance_map_condenser_liquid_pressure_differential
grid_variables |  | lookup_variables
condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | condenser_liquid_differential_pressure
m3/s | K | Pa
0.044304 | 285.9278 | 15000
0.044304 | 297.0389 | 15000
0.044304 | 308.15 | 15000
0.044304 | 319.2611 | 15000
Note on A2: Data group defining the grid variables for the condenser liquid pressure differential
Note on C2: Data group defining the lookup variables for the condenser liquid pressure differential
Note on A3: Condenser liquid flow
Note on B3: Entering condenser liquid temperature
Note on C3: Pressure difference across the condenser

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | oil_cooler_heat | auxiliary_heat | operation_state
m3/s | K | m3/s | K | - | W | W | W | W | W | -
0.033905 | 275.3722 | 0.044304 | 285.9278 | 1 | 40713.5336 | 185347.6417 | 226061.1754 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.044304 | 285.9278 | 2 | 58845.2869 | 370695.2835 | 429540.5704 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.044304 | 285.9278 | 3 | 82584.8389 | 556042.9252 | 638627.7642 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.044304 | 285.9278 | 4 | 111932.1896 | 741390.567 | 853322.7566 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.044304 | 297.0389 | 1 | 49313.1202 | 174280.2997 | 223593.4199 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.044304 | 297.0389 | 2 | 71274.6954 | 348560.5994 | 419835.2948 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.044304 | 297.0389 | 3 | 100028.5588 | 522840.8991 | 622869.4578 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.044304 | 297.0389 | 4 | 135574.7103 | 697121.1988 | 832695.909 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.044304 | 308.15 | 1 | 57543.4988 | 155348.8828 | 212892.3816 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.044304 | 308.15 | 2 | 83170.4693 | 310697.7656 | 393868.2349 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.044304 | 308.15 | 3 | 116723.3633 | 466046.6484 | 582770.0118 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.044304 | 308.15 | 4 | 158202.1811 | 621395.5313 | 779597.7123 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.044304 | 319.2611 | 1 | 61968.5836 | 128553.3911 | 190521.9747 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.044304 | 319.2611 | 2 | 89566.2635 | 257106.7823 | 346673.0457 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.044304 | 319.2611 | 3 | 125699.3691 | 385660.1734 | 511359.5425 | 0 | 0 | NORMAL
0.033905 | 275.3722 | 0.044304 | 319.2611 | 4 | 170367.9005 | 514213.5645 | 684581.465 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.044304 | 285.9278 | 1 | 44652.4476 | 223693.9506 | 268346.3982 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.044304 | 285.9278 | 2 | 64538.3944 | 447387.9011 | 511926.2955 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.044304 | 285.9278 | 3 | 90574.6778 | 671081.8517 | 761656.5295 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.044304 | 285.9278 | 4 | 122761.2979 | 894775.8023 | 1017537.1001 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.044304 | 297.0389 | 1 | 54047.4127 | 214259.6659 | 268307.0786 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.044304 | 297.0389 | 2 | 78117.4028 | 428519.3317 | 506636.7346 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.044304 | 297.0389 | 3 | 109631.7729 | 642778.9976 | 752410.7705 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.044304 | 297.0389 | 4 | 148590.5228 | 857038.6635 | 1005629.1863 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.044304 | 308.15 | 1 | 64811.8895 | 196961.3063 | 261773.1958 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.044304 | 308.15 | 2 | 93675.8343 | 393922.6127 | 487598.447 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.044304 | 308.15 | 3 | 131466.8361 | 590883.919 | 722350.7551 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.044304 | 308.15 | 4 | 178184.8947 | 787845.2254 | 966030.1201 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.044304 | 319.2611 | 1 | 73879.5676 | 171798.872 | 245678.4396 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.044304 | 319.2611 | 2 | 106781.7987 | 343597.744 | 450379.5427 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.044304 | 319.2611 | 3 | 149860.05 | 515396.6161 | 665256.6661 | 0 | 0 | NORMAL
0.033905 | 281.6685 | 0.044304 | 319.2611 | 4 | 203114.3217 | 687195.4881 | 890309.8098 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.044304 | 285.9278 | 1 | 47349.1798 | 231439.3479 | 278788.5276 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.044304 | 285.9278 | 2 | 68436.115 | 462878.6957 | 531314.8107 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.044304 | 285.9278 | 3 | 96044.8292 | 694318.0436 | 790362.8728 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.044304 | 285.9278 | 4 | 130175.3224 | 925757.3915 | 1055932.7139 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.044304 | 297.0389 | 1 | 55142.2207 | 223638.1205 | 278780.3413 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.044304 | 297.0389 | 2 | 79699.7831 | 447276.241 | 526976.0241 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.044304 | 297.0389 | 3 | 111852.522 | 670914.3616 | 782766.8835 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.044304 | 297.0389 | 4 | 151600.4374 | 894552.4821 | 1046152.9195 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.044304 | 308.15 | 1 | 65037.5523 | 207972.8184 | 273010.3707 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.044304 | 308.15 | 2 | 94001.996 | 415945.6367 | 509947.6327 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.044304 | 308.15 | 3 | 131924.5789 | 623918.4551 | 755843.034 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.044304 | 308.15 | 4 | 178805.301 | 831891.2734 | 1010696.5745 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.044304 | 319.2611 | 1 | 74338.6395 | 184443.4414 | 258782.0809 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.044304 | 319.2611 | 2 | 107445.3181 | 368886.8828 | 476332.2009 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.044304 | 319.2611 | 3 | 150791.2486 | 553330.3242 | 704121.5728 | 0 | 0 | NORMAL
0.033905 | 287.9648 | 0.044304 | 319.2611 | 4 | 204376.431 | 737773.7656 | 942150.1966 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.044304 | 285.9278 | 1 | 48928.6405 | 208583.8336 | 257512.4741 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.044304 | 285.9278 | 2 | 70718.9878 | 417167.6673 | 487886.6551 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.044304 | 285.9278 | 3 | 99248.6658 | 625751.5009 | 725000.1667 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.044304 | 285.9278 | 4 | 134517.6745 | 834335.3346 | 968853.0091 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.044304 | 297.0389 | 1 | 53823.1469 | 202415.6637 | 256238.8105 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.044304 | 297.0389 | 2 | 77793.2603 | 404831.3273 | 482624.5876 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.044304 | 297.0389 | 3 | 109176.8638 | 607246.991 | 716423.8547 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.044304 | 297.0389 | 4 | 147973.9572 | 809662.6546 | 957636.6118 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.044304 | 308.15 | 1 | 60546.7821 | 188383.4189 | 248930.2009 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.044304 | 308.15 | 2 | 87511.2633 | 376766.8377 | 464278.101 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.044304 | 308.15 | 3 | 122815.3343 | 565150.2566 | 687965.5908 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.044304 | 308.15 | 4 | 166458.995 | 753533.6754 | 919992.6704 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.044304 | 319.2611 | 1 | 66772.7865 | 166487.0992 | 233259.8858 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.044304 | 319.2611 | 2 | 96510.016 | 332974.1985 | 429484.2144 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.044304 | 319.2611 | 3 | 135444.3922 | 499461.2977 | 634905.6899 | 0 | 0 | NORMAL
0.033905 | 294.2611 | 0.044304 | 319.2611 | 4 | 183575.9153 | 665948.397 | 849524.3123 | 0 | 0 | NORMAL
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on J3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).
Note on K3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation