## RS0001
RS0001: Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 3.0.0 |  | ✓
| description | ASHRAE 90.1-2022 Appendix J curve set 'Y': 300.0+ ton, 5.50 COP, 6.15 IPLV liquid-cooled, positive displacement compressor chiller |  | ✓
| id | c18ff78a-b4c9-4e09-ab5d-973ed4be86e2 |  | ✓
| data_timestamp | 2025-02-18T13:40Z |  | ✓
| data_version | 3 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2022 Appendix J curve set 'Y' for Performance Rating Method (PRM)
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | SCROLL
performance |  |  |  | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| cycling_degradation_coefficient | 0 | - | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
performance.performance_map_evaporator_liquid_pressure_differential |  | $performance_map_evaporator_liqu |  | ✓
| condenser_type | LIQUID |  | ✓
performance.condenser_liquid_type
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| condenser_fouling_factor | 0 | m2-K/W
performance.performance_map_condenser_liquid_pressure_differential |  | $performance_map_condenser_liqui
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
performance.scaling
| minimum | 0.85714 | -
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on B20: Type of compressor speed control
Note on B21: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A22: Type of liquid in evaporator
Note on A23: An array of all liquid components within the liquid mixture
Note on B24: Defines whether concentration is defined on a volume or mass basis
Note on B25: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on A26: Data group describing the liquid pressure differential through the evaporator
Note on B27: Heat rejection method of the condenser
Note on A28: Type of liquid in condenser
Note on A29: An array of all liquid components within the liquid mixture
Note on B30: Defines whether concentration is defined on a volume or mass basis
Note on B31: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on A32: Data group describing the liquid pressure differential through the condenser
Note on A33: Data group describing cooling performance over a range of conditions
Note on A34: Data group describing standby performance
Note on A35: Specifies the range the performance data can be scaled to represent different capacity equipment
Note on B36: Minimum scaling factor

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_evaporator_liqu
performance.performance_map_evaporator_liquid_pressure_differential
grid_variables |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | evaporator_liquid_differential_pressure
m3/s | K | Pa
0.052741 | 275.3722 | 15000
0.052741 | 281.6685 | 15000
0.052741 | 287.9648 | 15000
0.052741 | 294.2611 | 15000
Note on A2: Data group defining the grid variables for the evaporator liquid pressure differential
Note on C2: Data group defining the lookup variables for the evaporator liquid pressure differential
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Pressure difference across the evaporator

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_condenser_liqui
performance.performance_map_condenser_liquid_pressure_differential
grid_variables |  | lookup_variables
condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | condenser_liquid_differential_pressure
m3/s | K | Pa
0.067643 | 285.9278 | 15000
0.067643 | 297.0389 | 15000
0.067643 | 308.15 | 15000
0.067643 | 319.2611 | 15000
Note on A2: Data group defining the grid variables for the condenser liquid pressure differential
Note on C2: Data group defining the lookup variables for the condenser liquid pressure differential
Note on A3: Condenser liquid flow
Note on B3: Entering condenser liquid temperature
Note on C3: Pressure difference across the condenser

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | oil_cooler_heat | auxiliary_heat | operation_state
m3/s | K | m3/s | K | - | W | W | W | W | W | -
0.052741 | 275.3722 | 0.067643 | 285.9278 | 1 | 65462.6575 | 289152.2863 | 354614.9438 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.067643 | 285.9278 | 2 | 88359.0218 | 578304.5727 | 666663.5944 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.067643 | 285.9278 | 3 | 124364.1498 | 867456.859 | 991821.0087 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.067643 | 285.9278 | 4 | 173478.0414 | 1156609.1453 | 1330087.1867 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.067643 | 297.0389 | 1 | 78077.9844 | 279498.4697 | 357576.4541 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.067643 | 297.0389 | 2 | 105386.7134 | 558996.9393 | 664383.6527 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.067643 | 297.0389 | 3 | 148330.3997 | 838495.409 | 986825.8086 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.067643 | 297.0389 | 4 | 206909.043 | 1117993.8786 | 1324902.9217 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.067643 | 308.15 | 1 | 86933.7152 | 261182.7735 | 348116.4887 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.067643 | 308.15 | 2 | 117339.8443 | 522365.547 | 639705.3912 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.067643 | 308.15 | 3 | 165154.2726 | 783548.3204 | 948702.593 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.067643 | 308.15 | 4 | 230377.0001 | 1044731.0939 | 1275108.094 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.067643 | 319.2611 | 1 | 90610.0102 | 234205.1978 | 324815.208 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.067643 | 319.2611 | 2 | 122301.9684 | 468410.3956 | 590712.364 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.067643 | 319.2611 | 3 | 172138.3964 | 702615.5934 | 874753.9898 | 0 | 0 | NORMAL
0.052741 | 275.3722 | 0.067643 | 319.2611 | 4 | 240119.2942 | 936820.7912 | 1176940.0854 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.067643 | 285.9278 | 1 | 64019.0616 | 329710.6549 | 393729.7165 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.067643 | 285.9278 | 2 | 86410.5106 | 659421.3098 | 745831.8203 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.067643 | 285.9278 | 3 | 121621.6461 | 989131.9647 | 1110753.6108 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.067643 | 285.9278 | 4 | 169652.4682 | 1318842.6195 | 1488495.0878 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.067643 | 297.0389 | 1 | 78067.7153 | 323888.8334 | 401956.5488 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.067643 | 297.0389 | 2 | 105372.8526 | 647777.6669 | 753150.5195 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.067643 | 297.0389 | 3 | 148310.8907 | 971666.5003 | 1119977.3911 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.067643 | 297.0389 | 4 | 206881.8296 | 1295555.3338 | 1502437.1634 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.067643 | 308.15 | 1 | 89244.2666 | 309405.1325 | 398649.3991 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.067643 | 308.15 | 2 | 120458.5393 | 618810.265 | 739268.8043 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.067643 | 308.15 | 3 | 169543.7944 | 928215.3975 | 1097759.1919 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.067643 | 308.15 | 4 | 236500.032 | 1237620.53 | 1474120.5619 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.067643 | 319.2611 | 1 | 96293.3498 | 286259.552 | 382552.9019 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.067643 | 319.2611 | 2 | 129973.1255 | 572519.1041 | 702492.2295 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.067643 | 319.2611 | 3 | 182935.4481 | 858778.6561 | 1041714.1042 | 0 | 0 | NORMAL
0.052741 | 281.6685 | 0.067643 | 319.2611 | 4 | 255180.3176 | 1145038.2082 | 1400218.5258 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.067643 | 285.9278 | 1 | 64240.1162 | 336330.7496 | 400570.8658 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.067643 | 285.9278 | 2 | 86708.8818 | 672661.4991 | 759370.3809 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.067643 | 285.9278 | 3 | 122041.5996 | 1008992.2487 | 1131033.8483 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.067643 | 285.9278 | 4 | 170238.2698 | 1345322.9983 | 1515561.2681 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.067643 | 297.0389 | 1 | 77492.7544 | 334340.9234 | 411833.6778 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.067643 | 297.0389 | 2 | 104596.7921 | 668681.8467 | 773278.6388 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.067643 | 297.0389 | 3 | 147218.5958 | 1003022.7701 | 1150241.3659 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.067643 | 297.0389 | 4 | 205358.1656 | 1337363.6934 | 1542721.8591 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.067643 | 308.15 | 1 | 88397.3406 | 323689.2176 | 412086.5582 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.067643 | 308.15 | 2 | 119315.3905 | 647378.4353 | 766693.8258 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.067643 | 308.15 | 3 | 167934.8277 | 971067.6529 | 1139002.4806 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.067643 | 308.15 | 4 | 234255.652 | 1294756.8706 | 1529012.5226 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.067643 | 319.2611 | 1 | 95862.9829 | 304375.6324 | 400238.6153 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.067643 | 319.2611 | 2 | 129392.2324 | 608751.2648 | 738143.4973 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.067643 | 319.2611 | 3 | 182117.8488 | 913126.8973 | 1095244.7461 | 0 | 0 | NORMAL
0.052741 | 287.9648 | 0.067643 | 319.2611 | 4 | 254039.8321 | 1217502.5297 | 1471542.3618 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.067643 | 285.9278 | 1 | 67025.2256 | 309012.5704 | 376037.796 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.067643 | 285.9278 | 2 | 90468.1173 | 618025.1408 | 708493.258 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.067643 | 285.9278 | 3 | 127332.6736 | 927037.7111 | 1054370.3848 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.067643 | 285.9278 | 4 | 177618.8948 | 1236050.2815 | 1413669.1763 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.067643 | 297.0389 | 1 | 78206.686 | 310854.7394 | 389061.4254 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.067643 | 297.0389 | 2 | 105560.43 | 621709.4788 | 727269.9088 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.067643 | 297.0389 | 3 | 148574.9034 | 932564.2182 | 1081139.1216 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.067643 | 297.0389 | 4 | 207250.1062 | 1243418.9576 | 1450669.0638 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.067643 | 308.15 | 1 | 87200.7015 | 304035.0289 | 391235.7304 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.067643 | 308.15 | 2 | 117700.2123 | 608070.0578 | 725770.2701 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.067643 | 308.15 | 3 | 165661.4857 | 912105.0868 | 1077766.5725 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.067643 | 308.15 | 4 | 231084.5218 | 1216140.1157 | 1447224.6375 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.067643 | 319.2611 | 1 | 93080.854 | 288553.4389 | 381634.2929 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.067643 | 319.2611 | 2 | 125637.02 | 577106.8779 | 702743.8978 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.067643 | 319.2611 | 3 | 176832.4372 | 865660.3168 | 1042492.754 | 0 | 0 | NORMAL
0.052741 | 294.2611 | 0.067643 | 319.2611 | 4 | 246667.1056 | 1154213.7557 | 1400880.8613 | 0 | 0 | NORMAL
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on J3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).
Note on K3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation