## RS0001
RS0001: Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model | ASHRAE_205 |  | ✓
| schema | RS0001 |  | ✓
| schema_version | 3.0.0 |  | ✓
| description | ASHRAE 90.1-2022 Appendix J curve set 'Z': 0.0-150.0 ton, 5.00 COP, 5.25 IPLV liquid-cooled, centrifugal compressor chiller |  | ✓
| id | cfc9ce09-06f6-467e-9a49-fc4621df8d5a |  | ✓
| data_timestamp | 2025-02-18T13:40Z |  | ✓
| data_version | 3 |  | ✓
| data_source | https://github.com/bigladder/chiller
| disclaimer | This data is synthetic and does not represent any physical products.
| notes | Based on ASHRAE 90.1-2022 Appendix J curve set 'Z' for Performance Rating Method (PRM)
description
description.product_information
| liquid_data_source | CoolProp
| hot_gas_bypass_installed | FALSE
| compressor_type | CENTRIFUGAL
performance |  |  |  | ✓
| compressor_speed_control_type | CONTINUOUS |  | ✓
| cycling_degradation_coefficient | 0 | - | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| evaporator_fouling_factor | 0 | m2-K/W | ✓
performance.performance_map_evaporator_liquid_pressure_differential |  | $performance_map_evaporator_liqu |  | ✓
| condenser_type | LIQUID |  | ✓
performance.condenser_liquid_type
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type | BY_VOLUME |  | ✓
| condenser_fouling_factor | 0 | m2-K/W
performance.performance_map_condenser_liquid_pressure_differential |  | $performance_map_condenser_liqui
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
performance.scaling
| maximum | 2 | -
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Description of data (suitable for display)
Note on B8: Unique equipment identifier
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Source of the liquid properties data
Note on B17: Indicates if a hot-gas bypass valve is installed on the chiller
Note on B18: Type of compressor
Note on A19: Data group containing performance information
Note on B20: Type of compressor speed control
Note on B21: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A22: Type of liquid in evaporator
Note on A23: An array of all liquid components within the liquid mixture
Note on B24: Defines whether concentration is defined on a volume or mass basis
Note on B25: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on A26: Data group describing the liquid pressure differential through the evaporator
Note on B27: Heat rejection method of the condenser
Note on A28: Type of liquid in condenser
Note on A29: An array of all liquid components within the liquid mixture
Note on B30: Defines whether concentration is defined on a volume or mass basis
Note on B31: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on A32: Data group describing the liquid pressure differential through the condenser
Note on A33: Data group describing cooling performance over a range of conditions
Note on A34: Data group describing standby performance
Note on A35: Specifies the range the performance data can be scaled to represent different capacity equipment
Note on B36: Maximum scaling factor

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_evaporator_liqu
performance.performance_map_evaporator_liquid_pressure_differential
grid_variables |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | evaporator_liquid_differential_pressure
m3/s | K | Pa
0.011302 | 275.3722 | 15000
0.011302 | 281.6685 | 15000
0.011302 | 287.9648 | 15000
0.011302 | 294.2611 | 15000
Note on A2: Data group defining the grid variables for the evaporator liquid pressure differential
Note on C2: Data group defining the lookup variables for the evaporator liquid pressure differential
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Pressure difference across the evaporator

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
WATER | 1
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_condenser_liqui
performance.performance_map_condenser_liquid_pressure_differential
grid_variables |  | lookup_variables
condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | condenser_liquid_differential_pressure
m3/s | K | Pa
0.014718 | 285.9278 | 15000
0.014718 | 297.0389 | 15000
0.014718 | 308.15 | 15000
0.014718 | 319.2611 | 15000
Note on A2: Data group defining the grid variables for the condenser liquid pressure differential
Note on C2: Data group defining the lookup variables for the condenser liquid pressure differential
Note on A3: Condenser liquid flow
Note on B3: Entering condenser liquid temperature
Note on C3: Pressure difference across the condenser

## performance_map_cooling
performance.performance_map_cooling
grid_variables |  |  |  |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | oil_cooler_heat | auxiliary_heat | operation_state
m3/s | K | m3/s | K | - | W | W | W | W | W | -
0.011302 | 275.3722 | 0.014718 | 285.9278 | 1 | 16055.4519 | 63365.5481 | 79421 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 0.014718 | 285.9278 | 2 | 22543.7205 | 126731.0961 | 149274.8166 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 0.014718 | 285.9278 | 3 | 31869.2584 | 190096.6442 | 221965.9026 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 0.014718 | 285.9278 | 4 | 44032.0657 | 253462.1922 | 297494.2579 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 0.014718 | 297.0389 | 1 | 17595.1377 | 58217.2655 | 75812.4033 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 0.014718 | 297.0389 | 2 | 24705.6183 | 116434.5311 | 141140.1494 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 0.014718 | 297.0389 | 3 | 34925.4567 | 174651.7966 | 209577.2534 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 0.014718 | 297.0389 | 4 | 48254.653 | 232869.0622 | 281123.7151 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 0.014718 | 308.15 | 1 | 17382.8693 | 53329.4907 | 70712.36 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 0.014718 | 308.15 | 2 | 24407.5688 | 106658.9814 | 131066.5502 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 0.014718 | 308.15 | 3 | 34504.1147 | 159988.472 | 194492.5867 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 0.014718 | 308.15 | 4 | 47672.507 | 213317.9627 | 260990.4697 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 0.014718 | 319.2611 | 1 | 15805.7331 | 48702.2235 | 64507.9566 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 0.014718 | 319.2611 | 2 | 22193.0863 | 97404.4469 | 119597.5332 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 0.014718 | 319.2611 | 3 | 31373.5793 | 146106.6704 | 177480.2497 | 0 | 0 | NORMAL
0.011302 | 275.3722 | 0.014718 | 319.2611 | 4 | 43347.212 | 194808.8939 | 238156.1059 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 0.014718 | 285.9278 | 1 | 16365.7955 | 74174.5886 | 90540.3841 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 0.014718 | 285.9278 | 2 | 22979.479 | 148349.1773 | 171328.6563 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 0.014718 | 285.9278 | 3 | 32485.2747 | 222523.7659 | 255009.0407 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 0.014718 | 285.9278 | 4 | 44883.1828 | 296698.3546 | 341581.5374 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 0.014718 | 297.0389 | 1 | 19011.5075 | 70534.8083 | 89546.3157 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 0.014718 | 297.0389 | 2 | 26694.3661 | 141069.6165 | 167763.9826 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 0.014718 | 297.0389 | 3 | 37736.8789 | 211604.4248 | 249341.3037 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 0.014718 | 297.0389 | 4 | 52139.046 | 282139.233 | 334278.279 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 0.014718 | 308.15 | 1 | 19696.3488 | 67155.5355 | 86851.8844 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 0.014718 | 308.15 | 2 | 27655.963 | 134311.0711 | 161967.034 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 0.014718 | 308.15 | 3 | 39096.2544 | 201466.6066 | 240562.8609 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 0.014718 | 308.15 | 4 | 54017.223 | 268622.1421 | 322639.3651 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 0.014718 | 319.2611 | 1 | 18693.6937 | 64036.7705 | 82730.4641 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 0.014718 | 319.2611 | 2 | 26248.1186 | 128073.5409 | 154321.6595 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 0.014718 | 319.2611 | 3 | 37106.0347 | 192110.3114 | 229216.346 | 0 | 0 | NORMAL
0.011302 | 281.6685 | 0.014718 | 319.2611 | 4 | 51267.4419 | 256147.0818 | 307414.5238 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 0.014718 | 285.9278 | 1 | 16000.8544 | 75666.8986 | 91667.753 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 0.014718 | 285.9278 | 2 | 22467.0592 | 151333.7972 | 173800.8564 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 0.014718 | 285.9278 | 3 | 31760.8851 | 227000.6958 | 258761.5809 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 0.014718 | 285.9278 | 4 | 43882.332 | 302667.5944 | 346549.9264 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 0.014718 | 297.0389 | 1 | 19148.679 | 73535.6204 | 92684.2994 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 0.014718 | 297.0389 | 2 | 26886.9709 | 147071.2407 | 173958.2116 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 0.014718 | 297.0389 | 3 | 38009.1576 | 220606.8611 | 258616.0186 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 0.014718 | 297.0389 | 4 | 52515.239 | 294142.4814 | 346657.7204 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 0.014718 | 308.15 | 1 | 20367.2691 | 71664.8498 | 92032.1188 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 0.014718 | 308.15 | 2 | 28598.013 | 143329.6995 | 171927.7125 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 0.014718 | 308.15 | 3 | 40427.997 | 214994.5493 | 255422.5463 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 0.014718 | 308.15 | 4 | 55857.2213 | 286659.399 | 342516.6204 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 0.014718 | 319.2611 | 1 | 19816.2861 | 70054.5868 | 89870.8729 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 0.014718 | 319.2611 | 2 | 27824.3688 | 140109.1736 | 167933.5425 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 0.014718 | 319.2611 | 3 | 39334.3237 | 210163.7605 | 249498.0842 | 0 | 0 | NORMAL
0.011302 | 287.9648 | 0.014718 | 319.2611 | 4 | 54346.1509 | 280218.3473 | 334564.4982 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 0.014718 | 285.9278 | 1 | 15322.555 | 67842.4779 | 83165.0329 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 0.014718 | 285.9278 | 2 | 21514.648 | 135684.9559 | 157199.6039 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 0.014718 | 285.9278 | 3 | 30414.4952 | 203527.4338 | 233941.929 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 0.014718 | 285.9278 | 4 | 42022.0964 | 271369.9117 | 313392.0081 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 0.014718 | 297.0389 | 1 | 18474.0816 | 67219.7018 | 85693.7835 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 0.014718 | 297.0389 | 2 | 25939.7578 | 134439.4036 | 160379.1614 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 0.014718 | 297.0389 | 3 | 36670.1159 | 201659.1055 | 238329.2214 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 0.014718 | 297.0389 | 4 | 50665.1561 | 268878.8073 | 319543.9634 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 0.014718 | 308.15 | 1 | 19968.5619 | 66857.4334 | 86825.9953 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 0.014718 | 308.15 | 2 | 28038.1817 | 133714.8667 | 161753.0485 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 0.014718 | 308.15 | 3 | 39636.5835 | 200572.3001 | 240208.8836 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 0.014718 | 308.15 | 4 | 54763.7672 | 267429.7335 | 322193.5006 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 0.014718 | 319.2611 | 1 | 19851.9449 | 66755.6726 | 86607.6175 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 0.014718 | 319.2611 | 2 | 27874.4379 | 133511.3451 | 161385.7831 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 0.014718 | 319.2611 | 3 | 39405.1047 | 200267.0177 | 239672.1224 | 0 | 0 | NORMAL
0.011302 | 294.2611 | 0.014718 | 319.2611 | 4 | 54443.9452 | 267022.6902 | 321466.6354 | 0 | 0 | NORMAL
Note on A2: Data group defining the grid variables for cooling performance
Note on F2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Condenser liquid flow
Note on D3: Entering condenser liquid temperature
Note on E3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on F3: Total power input
Note on G3: Refrigeration capacity
Note on H3: Condenser heat rejection
Note on I3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on J3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).
Note on K3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
293.15 | 0
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation