## RS0001
RS0001: Chiller
Data Group | Data Element | Value | Units | Required
metadata |  |  |  | ✓
| data_model |  |  | ✓
| schema |  |  | ✓
| schema_version | 3.0.0 |  | ✓
| id |  |  | ✓
| description |  |  | ✓
| data_timestamp |  |  | ✓
| data_version |  |  | ✓
data_source
disclaimer
notes
description
description.product_information
manufacturer
model_number
| nominal_voltage |  | V
| nominal_frequency |  | Hz
compressor_type
liquid_data_source
refrigerant
hot_gas_bypass_installed
description.rating_ahri_550_590
certified_reference_number
test_standard_year
rating_source
| net_refrigerating_capacity |  | Btu/h
| input_power |  | kW
| cop |  | -
| iplv_ip |  | -
| nplv_ip |  | -
description.rating_ahri_551_591
certified_reference_number
test_standard_year
rating_source
| net_refrigerating_capacity |  | kW
| input_power |  | kW
| cop |  | -
| iplv_si |  | -
| nplv_si |  | -
performance |  |  |  | ✓
| condenser_type | AIR |  | ✓
performance.evaporator_liquid_type |  |  |  | ✓
performance.evaporator_liquid_type.liquid_components |  | $liquid_components |  | ✓
| concentration_type |  |  | ✓
performance.condenser_liquid_type
performance.condenser_liquid_type.liquid_components |  | $liquid_components0 |  | ✓
| concentration_type |  |  | ✓
| evaporator_fouling_factor |  | m2-K/W | ✓
| condenser_fouling_factor |  | m2-K/W
| compressor_speed_control_type |  |  | ✓
| cycling_degradation_coefficient |  | - | ✓
performance.scaling
| minimum |  | -
| maximum |  | -
performance.performance_map_cooling |  | $performance_map_cooling |  | ✓
performance.performance_map_standby |  | $performance_map_standby |  | ✓
performance.performance_map_evaporator_liquid_pressure_differential |  | $performance_map_evaporator_liqu |  | ✓
performance.performance_map_condenser_liquid_pressure_differential |  | $performance_map_condenser_liqui
Note on A3: Metadata data group
Note on B4: Data model name
Note on B5: Schema name or identifier
Note on B6: The version of the schema the data complies with
Note on B7: Unique equipment identifier
Note on B8: Description of data (suitable for display)
Note on B9: Date of publication
Note on B10: Integer version identifier for the data in the representation
Note on B11: Source(s) of the data
Note on B12: Characterization of accuracy, limitations, and applicability of this data
Note on B13: Additional Information
Note on A14: Data group describing product and rating information
Note on A15: Data group describing product information
Note on B16: Manufacturer name
Note on B17: Model number
Note on B18: Unit nominal voltage
Note on B19: Unit nominal frequency
Note on B20: Type of compressor
Note on B21: Source of the liquid properties data
Note on B22: Refrigerant used in the chiller
Note on B23: Indicates if a hot-gas bypass valve is installed on the chiller
Note on A24: Data group containing information relevant to products rated under AHRI 550/590
Note on B25: AHRI certified reference number
Note on B26: Year of the AHRI test standard
Note on B27: Source of this rating data
Note on B28: Rated net refrigeration capacity
Note on B29: Combined power input of all components of the unit, including auxiliary power and excluding integral pumps
Note on B30: Ratio of the net refrigerating capacity to the total input power at the rating conditions
Note on B31: The Integrated Part-Load Value efficiency of merit calculated at the standard rating conditions
Note on B32: The Non-Standard Part-Load Value efficiency of merit calculated at the conditions other than the IPLV.IP conditions
Note on A33: Data group containing information relevant to products rated under AHRI 551/591
Note on B34: AHRI certified reference number
Note on B35: Year of the AHRI test standard
Note on B36: Source of this rating data
Note on B37: Rated net refrigeration capacity
Note on B38: Combined power input of all components of the unit, including auxiliary power and excluding integral pumps
Note on B39: Ratio of the net refrigerating capacity to the total input power at the rating conditions
Note on B40: The Integrated Part-Load Value efficiency of merit calculated at the standard rating conditions
Note on B41: The Non-Standard Part-Load Value efficiency of merit calculated at the conditions other than the IPLV.SI conditions
Note on A42: Data group containing performance information
Note on B43: Heat rejection method of the condenser
Note on A44: Type of liquid in evaporator
Note on A45: An array of all liquid components within the liquid mixture
Note on B46: Defines whether concentration is defined on a volume or mass basis
Note on A47: Type of liquid in condenser
Note on A48: An array of all liquid components within the liquid mixture
Note on B49: Defines whether concentration is defined on a volume or mass basis
Note on B50: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B51: Factor of heat transfer inhibition due to heat exchanger fouling layer
Note on B52: Type of compressor speed control
Note on B53: Cycling degradation coefficient (C~D~) as described in AHRI 550/590 or AHRI 551/591
Note on A54: Specifies the range the performance data can be scaled to represent different capacity equipment
Note on B55: Minimum scaling factor
Note on B56: Maximum scaling factor
Note on A57: Data group describing cooling performance over a range of conditions
Note on A58: Data group describing standby performance
Note on A59: Data group describing the liquid pressure differential through the evaporator
Note on A60: Data group describing the liquid pressure differential through the condenser

## liquid_components
performance.evaporator_liquid_type.liquid_components
liquid_constituent | concentration
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## liquid_components0
performance.condenser_liquid_type.liquid_components
liquid_constituent | concentration
Note on A2: Substance of this component of the mixture
Note on B2: Concentration of this component of the mixture

## performance_map_cooling
performance.performance_map_cooling
grid_variables | [5 empty] | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | condenser_air_entering_drybulb_temperature | condenser_air_entering_relative_humidity | ambient_pressure | compressor_sequence_number | input_power | net_evaporator_capacity | net_condenser_capacity | condenser_air_volumetric_flow_rate | oil_cooler_heat | auxiliary_heat | operation_state
m3/s | K | K | - | Pa | - | W | W | W | m3/s | W | W | -
Note on A2: Data group defining the grid variables for cooling performance
Note on G2: Data group defining the lookup variables for cooling performance
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Entering condenser air drybulb temperature
Note on D3: Entering condenser air relative humidity
Note on E3: Ambient pressure used to calculate the performance
Note on F3: Index indicating the relative capacity order of the compressor speed/stage expressed in order from lowest capacity (starting at 1) to highest capacity
Note on G3: Total power input
Note on H3: Refrigeration capacity
Note on I3: Condenser heat rejection
Note on J3: Condenser air flow
Note on K3: Heat transferred to another liquid crossing the control volume boundary from the chiller oil cooler.
Note on L3: Heat transferred to another liquid crossing the control volume boundary from the chiller auxiliaries (motor, motor controller, inverter drive, starter, etc).
Note on M3: The operation state at the operating conditions

## performance_map_standby
performance.performance_map_standby
grid_variables | lookup_variables
environment_dry_bulb_temperature | input_power
K | W
Note on A2: Data group defining the grid variables for standby performance
Note on B2: Data group defining the lookup variables for standby performance
Note on A3: Dry bulb temperature of the air in the environment of the chiller
Note on B3: Total power consumed in standby operation

## performance_map_evaporator_liqu
performance.performance_map_evaporator_liquid_pressure_differential
grid_variables |  | lookup_variables
evaporator_liquid_volumetric_flow_rate | evaporator_liquid_leaving_temperature | evaporator_liquid_differential_pressure
m3/s | K | Pa
Note on A2: Data group defining the grid variables for the evaporator liquid pressure differential
Note on C2: Data group defining the lookup variables for the evaporator liquid pressure differential
Note on A3: Chilled liquid (evaporator) flow
Note on B3: Leaving evaporator liquid temperature
Note on C3: Pressure difference across the evaporator

## performance_map_condenser_liqui
performance.performance_map_condenser_liquid_pressure_differential
grid_variables |  | lookup_variables
condenser_liquid_volumetric_flow_rate | condenser_liquid_entering_temperature | condenser_liquid_differential_pressure
m3/s | K | Pa
Note on A2: Data group defining the grid variables for the condenser liquid pressure differential
Note on C2: Data group defining the lookup variables for the condenser liquid pressure differential
Note on A3: Condenser liquid flow
Note on B3: Entering condenser liquid temperature
Note on C3: Pressure difference across the condenser